## M-Bus module
| M-Bus Protocol For electronic meters | Version 2.1
Technical description
Description of M-Bus module and different variants of the model. The alternating current single and three-phase static meter can be provided with an M-Bus communicationmodule.The M-Bus communication module (inside of a special DIN single-module housing) is mounted next to the meter. Make sure that the IR modules of the meter and communication module face each other.
M-Bus module
General data
- M-Bus module conforming to EN1434
- Wired by YCYM or J.Y(St)Y 2 x 2 x 0.8 mm strand double-pole cables.
- 2 screwed-on terminals on M-Bus module.
- Data baud rate can be selected between 300 and 9600 Baud.
- The Parameterization of the module can be configured via M-Bus. The parameters are stored permanently in the M-Bus module.
- If power is cut, all data will be saved in the M-Bus module (uP FLASH).
- Data transmission conforming to IEC 870-5
o Asynchronous serial transmission (Start - Stop): half-duplex.
o Data baud rate can be selected among 300, 600, 1200, 2400, 4800 and 9600 Baud.
o Character size: 11 Bit per character (1 start bit, 8 data bit, 1 even bit and 1 stop bit).
o Bit sequence: The character is transmitted starting from the least significant bit.
o Character controlled by even bit.
o Data block controlled by checksum.
- Current consumption of M-Bus module < 2.6 mA. Equal to two standard loads.
Addressing:
An unambiguous address must be given to connect an M-Bus communication module to the M-Bus network.
The M-Bus module has two types of addressing: one with secondary address and one with primary address.
The secondary address has 8 digits (00000000-99999999) and can be chosen freely while operating on the M-Bus.
The primary address can be chosen between 0 and 250 while operating on the M-Bus.
Both the primary and secondary address can only appear once in the M-Bus system.
Baud rate:
The baud rate can be set during operation on the M-Bus and can be selected between 300, 600, 1200, 2400, 4800 or 9600 Baud.
Reading data:
Reading data parameterization can be chosen on the M-Bus (pay attention to groups).

## Read-out data
| Read-out data |  |  | Version 2.1
Read-out data that can be parameterized
Data name | Type of data | Unit | Resolution | Number of Bytes
Identification of Parameter Set | INT6 | - | S0,S1,S2,S3,S4,S5 | 9
Active Energy Import Total | INT4 | Wh | 0.1 kWh | 6
Reactive Energy Import Total | INT4 | varh | 0.1 kWh | 8
Active Energy Import Phase L1 Tarif 1 | INT4 | Wh | 0.1 kWh | 9
Active Energy Import Phase L2 Tarif 1 | INT4 | Wh | 0.1 kWh | 9
Active Energy Import Phase L3 Tarif 1 | INT4 | Wh | 0.1 kWh | 9
Active Energy Import Total Tarif 1 | INT4 | Wh | 0.1 kWh | 7
Active Energy Import Phase L1 Tarif 2 | INT4 | Wh | 0.1 kWh | 9
Active Energy Import Phase L2 Tarif 2 | INT4 | Wh | 0.1 kWh | 9
Active Energy Import Phase L3 Tarif 2 | INT4 | Wh | 0.1 kWh | 9
Active Energy Import Total Tarif 2 | INT4 | Wh | 0.1 kWh | 7
Active Energy Export Phase L1 Tarif 1 | INT4 | Wh (-) | 0.1 kWh | 9
Active Energy Export Phase L2 Tarif 1 | INT4 | Wh (-) | 0.1 kWh | 9
Active Energy Export Phase L3 Tarif 1 | INT4 | Wh (-) | 0.1 kWh | 9
Active Energy Export Total Tarif 1 | INT4 | Wh (-) | 0.1 kWh | 7
Active Energy Export Phase L1 Tarif 2 | INT4 | Wh (-) | 0.1 kWh | 9
Active Energy Export Phase L2 Tarif 2 | INT4 | Wh (-) | 0.1 kWh | 9
Active Energy Export Phase L3 Tarif 2 | INT4 | Wh (-) | 0.1 kWh | 9
Active Energy Export Total Tarif 2 | INT4 | Wh (-) | 0.1 kWh | 7
Reactive Energy Import Phase L1 Tarif 1 | INT4 | varh | 0.1 kvarh | 10
Reactive Energy Import Phase L2 Tarif 1 | INT4 | varh | 0.1 kvarh | 10
Reactive Energy Import Phase L3 Tarif 1 | INT4 | varh | 0.1 kvarh | 10
Reactive Energy Import Total Tarif 1 | INT4 | varh | 0.1 kvarh | 8
Reactive Energy Import Phase L1 Tarif 2 | INT4 | varh | 0.1 kvarh | 10
Reactive Energy Import Phase L2 Tarif 2 | INT4 | varh | 0.1 kvarh | 10
Reactive Energy Import Phase L3 Tarif 2 | INT4 | varh | 0.1 kvarh | 10
Reactive Energy Import Total Tarif 2 | INT4 | varh | 0.1 kvarh | 8
Reactive Energy Export Phase L1 Tarif 1 | INT4 | varh (-) | 0.1 kvarh | 10
Reactive Energy Export Phase L2 Tarif 1 | INT4 | varh (-) | 0.1 kvarh | 10
Reactive Energy Export Phase L3 Tarif 1 | INT4 | varh (-) | 0.1 kvarh | 10
Reactive Energy Export Total Tarif 1 | INT4 | varh (-) | 0.1 kvarh | 8
Reactive Energy Export Phase L1 Tarif 2 | INT4 | varh (-) | 0.1 kvarh | 10
Reactive Energy Export Phase L2 Tarif 2 | INT4 | varh (-) | 0.1 kvarh | 10
Reactive Energy Export Phase L3 Tarif 2 | INT4 | varh (-) | 0.1 kvarh | 10
Reactive Energy Export Total Tarif 2 | INT4 | varh (-) | 0.1 kvarh | 8
Active Power Phase L1 | INT4 | W (+,-) | 0.001 kW | 8
Active Power Phase L2 | INT4 | W (+,-) | 0.001 kW | 8
Active Power Phase L3 | INT4 | W (+,-) | 0.001 kW | 8
Active Power Total | INT4 | W (+,-) | 0.001 kW | 6
Reactive Power Phase L1 | INT4 | var (+,-) | 0.001 kvar | 10
Reactive Power Phase L2 | INT4 | var (+,-) | 0.001 kvar | 10
Reactive Power Phase L3 | INT4 | var (+,-) | 0.001 kvar | 10
Reactive Power Total | INT4 | var (+,-) | 0.001 kvar | 8
Tariff presently operating | INT4 |  | Tariff 1 oder Tariff 2 | 4
Status Byte 4 (Range Overflow Alarms) | INT4 | - | - | 4
Apparent Power Phase L1 | INT4 | VA (+,-) | 0.001 kVA | 10
Apparent Power Phase L2 | INT1 | VA (+,-) | 0.001 kVA | 10
Apparent Power Phase L3 | INT1 | VA (+,-) | 0.001 kVA | 10
Apparent Power Total | INT4 | VA (+,-) | 0.001 kVA | 8
Voltage Phase L1 | INT4 | V | 0.1 V | 7
Voltage Phase L2 | INT4 | V | 0.1 V | 7
Voltage Phase L3 | INT4 | V | 0.1 V | 7
Voltage Total -> only single phase meter | INT2 | V | 0.1 V | (5)
Current Phase L1 | INT2 | mA (+,-) | 0.001 A | 8
Current Phase L2 | INT2 | mA (+,-) | 0.001 A | 8
Current Phase L3 | INT3 | mA (+,-) | 0.001 A | 8
Current Total | INT3 | mA (+,-) | 0.001 A | 6
Power factor cos φ Phase L1 | INT1 | Fo x 0.1 | 0.01 | 6
Power factor cos φ Phase L2 | INT1 | Fo x 0.1 | 0.01 | 6
Power factor cos φ Phase L3 | INT1 | Fo x 0.1 | 0.01 | 6
Power factor cos φ Total | INT1 | Fo x 0.1 | 0.01 | 4
Netfrequency | INT2 | Hz x 0.1 | 0.1 Hz | 5
Total: 503*
* Warning: It’s possible to Read-out in one Telegram a maximum of 240 Bytes.

## Parameter Set for Read-out Data
| Parameter Set for Read-out Data |  |  |  |  | Version 2.1
Structure of Parameter Set for Read-out Data possible
The Parameter Set identification is a INT6 type (6 Bytes) => S0S1S2S3S4S5 <=
| S0 = Parameterset 0 | S1 = Parameterset 1 | S2 = Parameterset 2 | S3 = Parameterset 3 | S4 = Parameterset 4 | S5 = Parameterset 5
| value: 00 – 7F | value: 00 – FF | value: 00 – FF | value: 00 – FF | value: 00 – FF | value: 00 – FF
xxxx xxx1b | Parameterset Identification | Imported active or reactive energy phase L1 Tariff 1 | Exported active or reactive energy phase L1 Tariff 1 or Imported active or reactive energy phase L1 Tariff 1 | Active power phase L1 or Imported or exported reactive energy phase L1 Tariff 1 | Voltage Phase L1 -> By single phase meter is this the Voltage Total | Current Phase L1
xxxx xx1xb | Byte 4 State (Overflow Range Alarms) | Imported active or reactive energy phase L2 Tariff 1 | Exported active or reactive energy phase L2 Tariff 1 or Imported active or reactive energy phase L2 Tariff 1 | Active power phase L2 or Imported or exported reactive energy phase L2 Tariff 1 | Voltage Phase L2 | Current Phase L2
xxxx x1xxb | Parameterset 1 -> Instead of imported active energy -> Imported reactive energy | Imported active or reactive energy phase L3 Tariff 1 | Exported active or reactive energy phase L3 Tariff 1 or Imported active or reactive energy phase L3 Tariff 1 | Active power phase L3 or Imported or exported reactive energy phase L3 Tariff 1 | Voltage Phase L3 | Current Phase L3
xxxx 1xxxb | Parameterset 2 -> Instead of exported active energy -> Imported reactive energy | Total imported active or reactive energy Tariff 1 | Total exported active or reactive energy Tariff 1 or Total imported active or reactive energy Tariff 1 | Total active power or Total imported or exported reactive energy Tariff 1 | Active Energy Import Total | Total Current
xxx1 xxxxb | Parameterset 2 -> Instead of exported active energy -> Exported reactive energy | Imported active or reactive energy phase L1 Tariff 2 | Exported active or reactive energy phase L1 Tariff 2 or Imported active or reactive energy phase L1 Tariff 2 | Active power phase L1 or Imported or exported reactive energy phase L1 Tariff 2 | Reactive Energy ImportTotal | Power factor cos phi Phase L1
xx1x xxxxb | Parameterset 3 -> Instead of active and reactive power -> Imported reactive power | Imported active or reactive energy phase L2 Tariff 2 | Exported active or reactive energy phase L2 Tariff 2 or Imported active or reactive energy phase L2 Tariff 2 | Active power phase L2 or Imported or exported reactive energy phase L2 Tariff 2 | Reserve | Power factor cos phi Phase L2
x1xx xxxxb | Parameterset 3 -> Instead of active and reactive power -> Exported reactive power | Imported active or reactive energy phase L3 Tariff 2 | Exported active or reactive energy phase L3 Tariff 2 or Imported active or reactive energy phase L3 Tariff 2 | Active power phase L3 or Imported or exported reactive energy phase L3 Tariff 2 | Netfrequency | Power factor cos phi Phase L3
1xxx xxxxb | Parameterset 3 -> Instead of reactive power -> Apparent power | Total imported active or reactive energy Tariff 2 | Total exported active or reactive energy Tariff 2 or Total imported active or reactive energy Tariff 2 | Total active power or Total imported or exported reactive energy Tariff 2 | Tariff presently operating | Total power factor cos phi
Default Parameter Set
These are set by the factory.
Default Parameter Set Identification (INT6 Typ) = 0B FF 88 FF 9F 0F
| S0 = Parameterset 0 | S1 = Parameterset 1 | S2 = Parameterset 2 | S3 = Parameterset 3 | S4 = Parameterset 4 | S5 = Parameterset 5
| value: 0B | value: FF | value: 88 | value: FF | value: 9F | value: 0F
Default value | 0000 1011b | 1111 1111b | 1000 1000b | 1111 1111b | 1001 1111b | 0000 1111b
| Parameterset Identification Status Byte 4 (Range Overflow Alarms) Parameterset 2 Instead of exported active energy ->Imported reactive energy | Active - Energy Import Phase L1 Tariff 1(1) Active - Energy Import Phase L2 Tariff 1(1) Active - Energy Import Phase L3 Tariff 1(1) Active - Energy Import Total Tariff 1 Active - Energy Import Phase L1 Tariff 2(1) Active - Energy Import Phase L2 Tariff 2(1) Active - Energy Import Phase L3 Tariff 2(1) Active - Energy Import Total Tariff 2 | Total imported reactive energy Tariff 1 Total imported reactive energy Tariff 2 | Active - Power Phase L1(1) Active - Power Phase L2(1) Active - Power Phase L3(1) Active - Power Total Reactive - Power Phase L1(1) Reactive - Power Phase L2(1) Reactive - Power Phase L3(1) Reactive - Power Total | Voltage Phase L1(1) or Voltage Total(2) Voltage Phase L2(1) Voltage Phase L3(1) Active - Energy Import Total Reactive Energy Import Total Tariff presently operating | Current Phase L1(1) Current Phase L2(1) Current Phase L3(1) Current Total
Total bytes | 13 |  | 16
Total bytes 3 Phase Energy meter |  | 68 |  | 68 | 39 | 30
Total bytes 1 Phase Energy meter |  | 14 |  | 14 | 23 | 6
Total: 3 phase energy meter = 224 Byte and single phase energy meter = 86 Byte.
(1) Not if single Phase
(2) Only if 3 Phase

## Primary and Secondary Address
| Primary and Secondary Address |  |  |  | Version 2.1
Primary Address (A-Field)
Field A (address field) contains the Primary Address of the M-Bus module and is used to identify that module.
Field A can have a value between 0 and 255.
Structure of Primary Address (A-Field)
A-Field (Hex) |  | Primary address | Description
0 |  | 0 | Factory setting
01 – FA |  | 1 - 250 | Settable primary addresses
FB, FC |  | 251, 252 | Reserved for future use
FD |  | 253 | Used for processes with secondary addresses
FE |  | 254 | Used to send information to all devices connected to the M-Bus network (Broadcast telegram). All the devices respond with a reception confirmation or with theirprimary address.
FF |  | 255 | Used to send information to all devices connected to the M-Bus network (Broadcast telegram). The telegrams with this addressing do not receive replies.
Secondary Address (UD)
If “FD” is set in A-field, the identification of the M-Bus module occurs on Secondary Address (UD):
Structure of Secondary Address (UD)
Identification number |  | Producer | Version | Medium
xxxxxxxx |  | mm mm | xx | 02
8-digit serial number of M-Bus module (secondary address) => 00000000 – 99999999 |  | 2 Byte constant | 1 Byte, firmware version => 01 - FF | 1 Byte, constant = electricity => 02
Wildcard
The M-Bus module reacts to the requests only if the constant parameters (manufacturer, version, medium)and the identification number coincide with those supplied.
"Wildcards" can be used in all 4 of these parameters.
The wildcard character is „F“.
Individual wildcards cannot be used for constant parameters.

## Telegrams Parameterization
| Telegrams Parameterization | [28 empty] | Version 2.1
Byte Nr.
|  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | Comments
Reset M-Bus module access counter (SND_UD) | Primary Address | Value (Hex) | 68 | 03 | 03 | 68 | 73 | xx | 50 | xx | 16 | [18 empty] | This telegram resets the M-Bus module access counter, which is set at “0”. The M-Bus module confirms correct reception by means of a reply composed of a single character (ACK = E5). If the telegram is not received properly, the M-Bus module sends no confirmation.
|  | Description | Start Character Long- Telegram | L- Field | L- Field Repetition | Start- Character Long- Telegram Repetition | C- Field, SND_UD | A- Field, Primary Address (00 – FF = 0 – 255) | CI- Field, Initialise M-Bus module (Set to „0“) | CS Checksum, summed up C-Field to CI- Field incl. | Stop Character
| Secondary Address | Value (Hex) | 68 | 0B | 0B | 68 | 73 | FD | 50 | "UD" | [7 empty] | xx | 16
|  | Description | Start Character Long- Telegram | L- Field | L- Field Repetition | Start- Character Long- Telegram Repetition | C- Field, SND_UD | A- Field, Primary Address to FD = Sekundary Address | CI- Field, Initialise M-Bus module (Set module called to „0“) | Secondary Address UD (Please see:: „Secondary Address UD“) | [7 empty] | CS Checksum, summed up by C-Field to UD incl. | Stop Character
Set baud rate (SND_UD) | Primary Address | Value (Hex) | 68 | 03 | 03 | 68 | 73 | xx | xx | xx | 16 | [18 empty] | This telegram sets the desired baud rate on the M-Bus module. The M-Bus module confirms correct reception by means of a reply composed of a single character (ACK = E5). If the telegram is not received properly, the M-Bus module sends no confirmation.The confirmation reply (ACK) is sent by the M-Bus module with the former baud rate. As soon as “ACK” is sent, the M-Bus module changes to the new baud rate that was set.
|  | Description | Start Character Long- Telegram | L- Field | L- Field Repetition | Start- Character Long- Telegram Repetition | C- Field, SND_UD | A- Field, Primary Address (00 – FF = 0 – 255) | CI- Field, Set new Baudrate B8: 300 Baud B9: 600 Baud BA: 1200 Baud BB: 2400 Baud BC: 4800 Baud BD: 9600 Baud | CS Check Sum summed up by C Field, A Field and CI Field | Stop Character
| Secondary Address | Value (Hex) | 68 | 0B | 0B | 68 | 73 | FD | xx | "UD" | [7 empty] | xx | 16
|  | Description | Start Character Long- Telegram | L- Field | L- Field Repetition | Start- Character Long- Telegram Repetition | C- Field, SND_UD | A- Field, Primary Address to FD = Sekundary Address | CI- Field, Set new Baudrate B8: 300 Baud B9: 600 Baud BA: 1200 Baud BB: 2400 Baud BC: 4800 Baud BD: 9600 Baud | Secondary Address UD (Please see:: „Secondary Address UD“) | [7 empty] | CS Check Sum summed up by C Field, A Field and CI Field | Stop Character
Set Parameter Set to Default Read-out Data (SND_UD) | Primary Address | Value (Hex) | 68 | 04 | 04 | 68 | 73 | xx | 51 | 7F | xx | 16 | [17 empty] | This Telegram sets the Parameter Set for the Read-out Data of the Default Parameter Set. The M-Bus module confirms the correct receipt by Single Character Acknowledgement (ACK = E5). If the Telegram has not been correctly received, the M- Bus module will not send an Acknowledgement.
|  | Description | Start Character Long- Telegram | L- Field | L- Field Repetition | Start- Character Long- Telegram Repetition | C- Field, SND_UD | A- Field, Primary Address (00 – FF = 0 – 255) | CI- Field, New Data from M-Bus Modul | DIF- Field, Set Default Parameterset | CS Checksum, summed up by C-Field to DIF- Field incl. | Stop Character
| Secondary Address | Value (Hex) | 68 | 0C | 0C | 68 | 73 | FD | 51 | "UD" | [7 empty] | 7F | xx | 16
|  | Description | Start Character Long- Telegram | L- Field | L- Field Repetition | Start- Character Long- Telegram Repetition | C- Field, SND_UD | A- Field, Primary Address to FD = Sekundary Address | CI- Field, New Data from M-Bus Modul | Secondary Address UD (Please see:: „Secondary Address UD“) | [7 empty] | DIF- Field, Set Default Parameterset | CS Checksum, summed up by C-Field to DIF- Field incl. | Stop Character
Set Parameter Set to any Read-out Data desired (SND_UD) | Primary Address | Value (Hex) | 68 | 0C | 0C | 68 | 73 | xx | 51 | 06 | FD | 0B | "S0" | "S1" | "S2" | "S3" | "S4" | "S5" | xx | 16 | [9 empty] | This Telegram sets the Parameter Set for Read-out Data of any value desired. For the Structure of the Parameter Set for Read-out Data please see: „Structure of Parameter Set for Read-out Data possible“. The M-Bus module confirms the correct receipt by Single Character Acknowledgement (ACK = E5). If the telegram has not been correctly received the M-Bus module will not send an Acknowledgement. | (1)Please see: Parameter Set of Read-out Data
|  | Description | Start Character Long- Telegram | L- Field | L- Field Repetition | Start- Character Long- Telegram Repetition | C- Field, SND_UD | A- Field, Primary Address (00 – FF = 0 – 255) | CI- Field, New Data from M-Bus Modul | DIF- Field, 48 Bit Integer- Daten (6 Byte) | VIF- Field, Es folgt ein Standart VIFE | VIFE- Field, Std. VIFE = Parameterset- Identification | Parameter Set S0 (00 – FF) (1) | Parameter Set S1 (00 – FF) (1) | Parameter Set S2 (00 – FF) (1) | Parameter Set S3 (00 – FF) (1) | Parameter Set S4 (00 – FF) (1) | Parameter Set S5 (00 – FF) (1) | CS Checksum, summed up by C-Field to „S5“ incl. | Stop Character
| Secondary Address | Value (Hex) | 68 | 14 | 14 | 68 | 73 | FD | 51 | "UD" | [7 empty] | 06 | FD | 0B | "S0" | "S1" | "S2" | "S3" | "S4" | "S5" | xx | 16
|  | Description | Start Character Long- Telegram | L- Field | L- Field Repetition | Start- Character Long- Telegram Repetition | C- Field, SND_UD | A- Field, Primary Address to FD = Sekundary Address | CI- Field, New Data from M-Bus Modul | Secondary Address UD (Please see:: „Secondary Address UD“) | [7 empty] | DIF- Field, 48 Bit Integer- Daten (6 Byte) | VIF- Field, Es folgt ein Standart VIFE | VIFE- Field, Std. VIFE = Parameterset- Identification | Parameter Set S0 (00 – FF) (1) | Parameter Set S1 (00 – FF) (1) | Parameter Set S2 (00 – FF) (1) | Parameter Set S3 (00 – FF) (1) | Parameter Set S4 (00 – FF) (1) | Parameter Set S5 (00 – FF) (1) | CS Checksum, summed up by C-Field to „S5“ incl. | Stop Character
Set Primary Address (SND_UD) | Primary Address | Value (Hex) | 68 | 06 | 06 | 68 | 73 | xx | 51 | 01 | 7A | xx | xx | 16 | [15 empty] | This Telegram sets a new Primary Address in the M-Bus module. The M-Bus module confirms the correct receipt by Single Character Acknowledgement (ACK = E5). If the telegram has not been correctly received the M-Bus module will not send an Acknowledgement
|  | Description | Start Character Long- Telegram | L- Field | L- Field Repetition | Start- Character Long- Telegram Repetition | C- Field, SND_UD | A- Field, Primary Address (00 – FF = 0 – 255) | CI- Field, New Data from M-Bus Modul | DIF- Field, 8 Bit Integer - Data (1 Byte) | VIF- Field, Set Primary Address | New Primary Address: Range: 00 – FA (0 – 250), Invalid : FB – FF (no action in meter) | CS Checksum, summed up aus C-Field from C Field to Primary Address incl. | Stop Character
| Secondary Address | Value (Hex) | 68 | 0E | 0E | 68 | 73 | FD | 51 | "UD" | [7 empty] | 01 | 7A | xx | xx | 16
|  | Description | Start Character Long- Telegram | L- Field | L- Field Repetition | Start- Character Long- Telegram Repetition | C- Field, SND_UD | A- Field, Primary Address to FD = Sekundary Address | CI- Field, New Data from M-Bus Modul | Secondary Address UD (Please see:: „Secondary Address UD“) | [7 empty] | DIF- Field, 8 Bit Integer - Data (1 Byte) | VIF- Field, Set Primary Address | New Primary Address: Range: 00 – FA (0 – 250), Invalid : FB – FF (no action in meter) | CS Checksum, summed up aus C-Field from C Field to Primary Address incl. | Stop Character
Set Secondary Address (SND_UD) | Primary Address | Value (Hex) | 68 | 09 | 09 | 68 | 73 | xx | 51 | 0C | 79 | xx | xx | xx | xx | xx | 16 | [12 empty] | This Telegram sets a new Secondary Address in the M-Bus module. The M-Bus module confirms the correct receipt by Single Character Acknowledgement (ACK = E5). If the telegram has not been correctly received the M-Bus module will not send an Acknowledgement.
|  | Description | Start Character Long- Telegram | L- Field | L- Field Repetition | Start- Character Long- Telegram Repetition | C- Field, SND_UD | A- Field, Primary Address (00 – FF = 0 – 255) | CI- Field, New Data from M-Bus Modul | DIF- Field, 8 digits BCD, 4 Byte | VIF- Field, Set Secondary Address | New Secondary Address digit 7 and 8, Range: 00 - 99 | New Secondary Address digit 5 and 6, Range: 00 - 99 | New Secondary Address digit 3 and 4, Range: 00 - 99 | New Secondary Address digit 1 and 2, Range: 00 - 99 | CS Checksum, summed up from C Field up to Sec. Address incl. | Stop Character
| Secondary Address | Value (Hex) | 68 | 11 | 11 | 68 | 73 | FD | 51 | "UD" | [7 empty] | 0C | 79 | xx | xx | xx | xx | xx | 16
|  | Description | Start Character Long- Telegram | L- Field | L- Field Repetition | Start- Character Long- Telegram Repetition | C- Field, SND_UD | A- Field, Primary Address to FD = Sekundary Address | CI- Field, New Data from M-Bus Modul | Secondary Address UD (Please see:: „Secondary Address UD“) | [7 empty] | DIF- Field, 8 digits BCD, 4 Byte | VIF- Field, Set Secondary Address | New Secondary Address digit 7 and 8, Range: 00 - 99 | New Secondary Address digit 5 and 6, Range: 00 - 99 | New Secondary Address digit 3 and 4, Range: 00 - 99 | New Secondary Address digit 1 and 2, Range: 00 - 99 | CS Checksum, summed up from C Field up to Sec. Address incl. | Stop Character
Set Secondary Address and Manufacturer’s Mark (SND_UD) | Primary Address | Value (Hex) | 68 | 0D | 0D | 68 | 73 | xx | 51 | 07 | 79 | xx | xx | xx | xx | xx | xx | xx | xx | xx | 16 | [8 empty] | This Telegram sets a new Secondary Address and a new Manufacturer’s Mark. The M-Bus module confirms the correct receipt by Single Character Acknowledgement (ACK = E5). If the telegram has not been correctly received the M-Bus module will not send an Acknowledgement.
|  | Description | Start Character Long- Telegram | L- Field | L- Field Repetition | Start- Character Long- Telegram Repetition | C- Field, SND_UD | A- Field, Primary Address (00 – FF = 0 – 255) | CI- Field, New Data from M-Bus Modul | DIF- Field, 64 Bit Integer, 8 Byte | VIF- Field, Set Secondary Address and Manufacturer’s Mark | New Secondary Address digit 7 and 8, Range: 00 - 99 | New Secondary Address digit 5 and 6, Range: 00 - 99 | New Secondary Address digit 3 and 4, Range: 00 - 99 | New Secondary Address digit 1 and 2, Range: 00 - 99 | New Manufacturer’s Mark Byte 2, Range: 00 – FF | New Manufacturer’s Mark Byte 1, Range: 00 – FF | Version; This Parameter cannot be changed => Setting: Any Value 00 – FF | Medium; This Parameter is fixed to 02 and cannot be changed. => Setting: Any Value 00 - FF. | CS Checksum, summed up from C Field to Medium inclusive | Stop Character
| Secondary Address | Value (Hex) | 68 | 15 | 15 | 68 | 73 | FD | 51 | "UD" | [7 empty] | 07 | 79 | xx | xx | xx | xx | xx | xx | xx | xx | xx | 16
|  | Description | Start Character Long- Telegram | L- Field | L- Field Repetition | Start- Character Long- Telegram Repetition | C- Field, SND_UD | A- Field, Primary Address to FD = Sekundary Address | CI- Field, New Data from M-Bus Modul | Secondary Address UD (Please see:: „Secondary Address UD“) | [7 empty] | DIF- Field, 64 Bit Integer, 8 Byte | VIF- Field, Set Secondary Address and Manufacturer’s Mark | New Secondary Address digit 7 and 8, Range: 00 - 99 | New Secondary Address digit 5 and 6, Range: 00 - 99 | New Secondary Address digit 3 and 4, Range: 00 - 99 | New Secondary Address digit 1 and 2, Range: 00 - 99 | New Manufacturer’s Mark Byte 2, Range: 00 – FF | New Manufacturer’s Mark Byte 1, Range: 00 – FF | Version; This Parameter cannot be changed => Setting: Any Value 00 – FF | Medium; This Parameter is fixed to 02 and cannot be changed. => Setting: Any Value 00 - FF. | CS Checksum, summed up from C Field to Medium inclusive | Stop Character
Reset Active Energy Tariff 1 + 2 and Reactive Energy Tariff 1 + 2 (SND_UD) | Primary Address | Value (Hex) | 68 | 07 | 07 | 68 | 73 | xx | 51 | 01 | FF | 13 | xx | xx | 16 | [14 empty] | This Telegram enables to either Re-setting the Active Energy Tariff 1 + 2 in the M-Bus module and/or to Resetting the Reactive Energy Tariff 1 + 2 (Set to “0”). The M-Bus module confirms the correct receipt by Single Character Acknowledgement (ACK = E5). If the telegram has not been correctly received the M-Bus module will not send an Acknowledgement. Caution: This function is blocked in Electricity Meters with official certification (Metas or PTB Approval). | (2) Coding off Active and Reactive Energy Reset: 00h: No Reset Active and Reactive Energy (Binary: 0000 0000) 01h: Reset Active Energy (Binary: 0000 0001) 10h: Reset Reactive Energy (Binary: 0001 0000) 11h: Reset Reset Active and Reactive Energy (Binary: 0001 0001)
|  | Description | Start Character Long- Telegram | L- Field | L- Field Repetition | Start- Character Long- Telegram Repetition | C- Field, SND_UD | A- Field, Primary Address (00 – FF = 0 – 255) | CI- Field, New Data from M-Bus Modul | DIF- Field, 8 Bit Integer (1 Byte) | VIF- Field, An Manufacturer-spec.VIFE follows | VIFE- Field, Manufacturer-spec.VIFE = Energy Reset | Coding off Active and Reactive Energy Reset (2) | CS Checksum, summed up from C-Field to Coding | Stop Character
| Secondary Address | Value (Hex) | 68 | 0F | 0F | 68 | 73 | FD | 51 | "UD" | [7 empty] | 01 | FF | 13 | xx | xx | 16
|  | Description | Start Character Long- Telegram | L- Field | L- Field Repetition | Start- Character Long- Telegram Repetition | C- Field, SND_UD | A- Field, Primary Address to FD = Sekundary Address | CI- Field, New Data from M-Bus Modul | Secondary Address UD (Please see:: „Secondary Address UD“) | [7 empty] | DIF- Field, 8 Bit Integer (1 Byte) | VIF- Field, An Manufacturer-spec.VIFE follows | VIFE- Field, Manufacturer-spec.VIFE = Energy Reset | Coding off Active and Reactive Energy Reset (2) | CS Checksum, summed up from C-Field to Coding | Stop Character
Select M-Bus Module using Secondary Address (SND_UD) | Secondary Address | Value (Hex) | 68 | 0B | 0B | 68 | 73 | FD | 52 | "UD" | [19 empty] | This Telegram selects M-Bus module. The M-Bus module confirms the correct receipt by Single Character Acknowledgement (ACK = E5) and switch into Selection Mode. If the telegram has not been correctly received the M-Bus module will not send an Acknowledgement. In Selection Mode the M-Bus module is ready to transmit the entire Read-out Data after receiving the Telegram „Transmit Read-out Data“ (Short Telegram REQ_UD2 with A- Field on FD). In Selection Mode the M-Bus module accepts also all telegrams with Primary Address on FD (A-Field on FD) The M-Bus module switch back to Normal Mode by receiving an invalid telegram or by receiving the telegram “ Initialisation of M-Bus module”
|  | Description | Start Character Long- Telegram | L- Field | L- Field Repetition | Start- Character Long- Telegram Repetition | C- Field, SND_UD | A- Field, Primary Address to FD = Sekundary Address | CI- Field, New Data from M-Bus Modul | Secondary Address UD (Please see:: „Secondary Address UD“)

## Transmit Read-out Data
| Transmit Read-out Data | [22 empty] | Version 2.1
Transmit Read-out Data (REQ_UD2)
The M-Bus module receives this Short Telegram and transmits the parametrized Read-out Data. The M-Bus module confirms correct receipt by transmitting of the Read-out Data. If the Short Telegram has not been received correctly, no Data will be transmitted by the M-Bus module. The Read-out Data are sent within 35 – 75 ms from receipt of the Short Telegram by the M-Bus module.
Byte Nr.
|  | 1 | 2 | 3 |  |  | 4 | 5
Transmit Read-out Data | Value (Hex) | 10 | 7B | xx |  |  | xx | 16
| Description | Start Character Short Telegram | C- Field, Transmit Read-out Data | A- Field, Primary Address 00 – FA : Valid Primary Address FB, FC : Reserved for future use FD : Transmission using Secondary Address FE : All M-Bus module in the System transmit the Read-out Data FF : No action by M-Bus module |  |  | CS Checksum, summed up by C-Field and A- Field | Stop Character
Byte Nr.
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | … | YY | YY+1 | YY+2
Telegram of Read-out Data by M-Bus module (RSP_UD) | Value (Hex) | 68 | xx | xx | 68 | 08 | xx | 72 | xxxxxxxx |  |  |  | xxxx |  | xx | 02 | xx | xx | 00 00 |  | 00 - EA |  |  | xx | 16
| Description | Start Character Long- Telegram | L- Field, corresponding to number of Read-out Data parametrised | L- Field Repetition | Start Character Long Telegram Repetition | C- Field, Transmit Data of M-Bus module | A- Field, Primary Address (00 – FA = 0 – 250) | CI- Field, Read-out Data of M-Bus module | 8-digit Serial Number of M-Bus module (Sec. Address) |  |  |  | Manufacturer’s Mark |  | Version Number of M-Bus module Firmware (00 – FF) | Medium Electricity | Meter called upon, at each call on M-Bus module + 1 (00 – FF -> 00) | Shows the M-Bus module Status.(1) | Signature. For M-Bus module always on „0000“ |  | Read-out Data parametrised.(2) |  |  | CS Check Sum, summed up from C Field to End of „Read-out Data parametrised” | Stop Character
(1) Please see „Structure of Error Flags"
(2) Please see: ” Parameter Set for Read-out Data“
- Bytes No. 8 – 19 are the firm Data Record Header for every M-Bus module.
- Bytes No. 20 – YY are the Read-out Data defined in the Parameter Set.

## Telegram for Read-out Data
| Telegram for Read-out Data | [9 empty] | Version 2.1
The M-Bus module transmits Read-out Data to the Master depending on the Parameter Set. A summary of the options is shown under „ Parameterset for Read-out Data possible“.
Byte Nr.
|  | YY | YY+1 | YY+2 | YY+3 | YY+4 | YY+5 | YY+6 | YY+7 | YY+8 | YY+9 | YY+10
Parameterset Identification | Value (Hex) | 06 | FD | 0B | "S0" | "S1" | "S2" | "S3" | "S4" | "S5"
| Description | DIF, 48 Bit Integer, 6 Byte | VIF, followed by a Standart VIFE | Parameterset Identification | Parameterset S0 (00 – FF)(1) | Parameterset S1 (00 – FF)(1) | Parameterset S2 (00 – FF)(1) | Parameterset S3 (00 – FF)(1) | Parameterset S4 (00 – FF)(1) | Parameterset S5 (00 – FF)(1) |  |  | (1)Parameter Set for Read-out Data
Active Energy Import Total | Value (Hex) | 04 | 03 | xx | xx | xx | xx
| Description | DIF, 32 Bit Integer, 4 Byte | VIF, Active Energy Total | Active Energy Import Total
Reactive Energy Import Total | Value (Hex) | 84 | 80 | 40 | 03 | xx | xx | xx | xx
| Description | DIF, 32 Bit Integer, 4 Byte; Followed by a DIFE | DIFE, Followed by a further DIFE | DIFE, Reactive Register | VIF, Reactive Energy Total | Reactive Energy Import Total
Active Energy Import Phase L1, L2 and L3 Tariff 1 | Value (Hex) | 84 | 10 | 83 | FF | 0x | xx | xx | xx | xx
| Description | DIF, 32 Bit Integer, 4 Byte; Followed by a DIFE | DIFE, Tariff 1 | VIF, Active Energy, Followed by a further VIFE | VIFE, Followed by an Manufacturer-spec.VIFE | Manufacturer-spec.VIFE: 01 : Phase L1 02 : Phase L2 03 : Phase L3 | Active Energy Import Phase L1, L2 or L3
Active Energy Import Total Tariff 1 | Value (Hex) | 84 | 10 | 03 | xx | xx | xx | xx
| Description | DIF, 32 Bit Integer, 4 Byte; Followed by a DIFE | DIFE, Tariff 1 | VIF, Active Energy | Active Energy Import Total Tariff 1
Active Energy Import Phase L1 , L2 and L3 Tariff 2 | Value (Hex) | 84 | 20 | 83 | FF | 0x | xx | xx | xx | xx
| Description | DIF, 32 Bit Integer, 4 Byte; Followed by a DIFE | DIFE, Tariff 2 | VIF, Active Energy, Followed by a further VIFE | VIFE, Followed by an Manufacturer-spec.VIFE | Manufacturer-spec.VIFE: 01 : Phase L1 02 : Phase L2 03 : Phase L3 | Active Energy Import Phase L1, L2 or L3
Active Energy Import Total Tariff 2 | Value (Hex) | 84 | 20 | 03 | xx | xx | xx | xx
| Description | DIF, 32 Bit Integer, 4 Byte; Followed by a DIFE | DIFE, Tariff 2 | VIF, Active Energy | Active Energy Import Total Tariff 2
Active Energy Export Phase L1, L2 and L3 Tariff 1 | Value (Hex) | 84 | 10 | 83 | FF | 0x | xx | xx | xx | xx
| Description | DIF, 32 Bit Integer, 4 Byte; Followed by a DIFE | DIFE, Tariff 1 | VIF, Active Energy, Followed by a further VIFE | VIFE, Followed by an Manufacturer-spec.VIFE | Manufacturer-spec.VIFE: 01 : Phase L1 02 : Phase L2 03 : Phase L3 | Active Energy Export Phase L1, L2 or L3 -> IntegerValue = Negative
Active Energy Export Total Tariff 1 | Value (Hex) | 84 | 10 | 03 | xx | xx | xx | xx
| Description | DIF, 32 Bit Integer, 4 Byte; Followed by a DIFE | DIFE, Tariff 1 | VIF, Active Energy | Active Energy Export Total -> IntegerValue = Negative
Active Energy Export Phase L1, L2 and L3 Tariff 2 | Value (Hex) | 84 | 20 | 83 | FF | 0x | xx | xx | xx | xx
| Description | DIF, 32 Bit Integer, 4 Byte; Followed by a DIFE | DIFE, Tariff 2 | VIF, Active Energy, Followed by a further VIFE | VIFE, Followed by an Manufacturer-spec.VIFE | Manufacturer-spec.VIFE: 01 : Phase L1 02 : Phase L2 03 : Phase L3 | Active Energy Export Phase L1, L2 or L3 -> IntegerValue = Negative
Active Energy Export Total Tariff 2 | Value (Hex) | 84 | 20 | 03 | xx | xx | xx | xx
| Description | DIF, 32 Bit Integer, 4 Byte; Followed by a DIFE | DIFE, Tariff 2 | VIF, Active Energy | Active Energy Export Total -> IntegerValue = Negative
Reactive Energy Import Phase L1, L2 and L3 Tariff 1 | Value (Hex) | 84 | 90 | 40 | 83 | FF | 0x | xx | xx | xx | xx
| Description | DIF, 32 Bit Integer, 4 Byte; Followed by a DIFE | DIFE, Tariff 1 ; Followed by a further DIFE | DIFE, Reactive Value | VIF, Reactive Energy; Followed by a further VIFE | VIFE, Followed by an Manufacturer-spec.VIFE | Manufacturer-spec.VIFE: 01 : Phase L1 02 : Phase L2 03 : Phase L3 | Reactive Energy Import Phase L1, L2 or L3
Reactive Energy Import Total Tariff 1 | Value (Hex) | 84 | 90 | 40 | 03 | xx | xx | xx | xx
| Description | DIF, 32 Bit Integer, 4 Byte; Followed by a DIFE | DIFE, Tariff 1 ; Followed by a further DIFE | DIFE, Reactive Value | VIF, Reactive Energy | Reactive Energy Import Total
Reactive Energy Import Phase L1, L2 and L3 Tariff 2 | Value (Hex) | 84 | A0 | 40 | 83 | FF | 0x | xx | xx | xx | xx
| Description | DIF, 32 Bit Integer, 4 Byte; Followed by a DIFE | DIFE, Tariff 2 ; Followed by a further DIFE | DIFE, Reactive Value | VIF, Reactive Energy; Followed by a further VIFE | VIFE, Followed by an Manufacturer-spec.VIFE | Manufacturer-spec.VIFE: 01 : Phase L1 02 : Phase L2 03 : Phase L3 | Reactive Energy Import Phase L1, L2 or L3
Reactive Energy Import Total Tariff 2 | Value (Hex) | 84 | A0 | 40 | 03 | xx | xx | xx | xx
| Description | DIF, 32 Bit Integer, 4 Byte; Followed by a DIFE | DIFE, Tariff 2 ; Followed by a further DIFE | DIFE, Reactive Value | VIF, Reactive Energy | Reactive Energy Import Total
Reactive Energy Export Phase L1, L2 and L3 Tariff 1 | Value (Hex) | 84 | 90 | 40 | 83 | FF | 0x | xx | xx | xx | xx
| Description | DIF, 32 Bit Integer, 4 Byte; Followed by a DIFE | DIFE, Tariff 1 ; Followed by a further DIFE | DIFE, Reactive Value | VIF, Reactive Energy; Followed by a further VIFE | VIFE, Followed by an Manufacturer-spec.VIFE | Manufacturer-spec.VIFE: 01 : Phase L1 02 : Phase L2 03 : Phase L3 | Reactive Energy Export Phase L1, L2 or L3 -> IntegerValue = Negative
Reactive Energy Export Total Tariff 1 | Value (Hex) | 84 | 90 | 40 | 03 | xx | xx | xx | xx
| Description | DIF, 32 Bit Integer, 4 Byte; Followed by a DIFE | DIFE, Tariff 1 ; Followed by a further DIFE | DIFE, Reactive Value | VIF, Reactive Energy | Reactive Energy Export Total -> IntegerValue = Negative
Reactive Energy Export Phase L1, L2 and L3 Tariff 2 | Value (Hex) | 84 | A0 | 40 | 83 | FF | 0x | xx | xx | xx | xx
| Description | DIF, 32 Bit Integer, 4 Byte; Followed by a DIFE | DIFE, Tariff 2 ; Followed by a further DIFE | DIFE, Reactive Value | VIF, Reactive Energy; Followed by a further VIFE | VIFE, Followed by an Manufacturer-spec.VIFE | Manufacturer-spec.VIFE: 01 : Phase L1 02 : Phase L2 03 : Phase L3 | Reactive Energy Export Phase L1, L2 or L3 -> IntegerValue = Negative
Reactive Energy Export Total Tariff 2 | Value (Hex) | 84 | A0 | 40 | 03 | xx | xx | xx | xx
| Description | DIF, 32 Bit Integer, 4 Byte; Followed by a DIFE | DIFE, Tariff 2 ; Followed by a further DIFE | DIFE, Reactive Value | VIF, Reactive Energy | Reactive Energy Export Total -> IntegerValue = Negative
Active Power Phase L1, L2 and L3 | Value (Hex) | 04 | AB | FF | 0x | xx | xx | xx | xx
| Description | DIF, 32 Bit Integer, 4 Byte | VIF, Active Power; Followed by a further VIFE | VIFE, Followed by an Manufacturer-spec.VIFE | Manufacturer-spec.VIFE: 01 : Phase L1 02 : Phase L2 03 : Phase L3 | Active Power Phase L1, L2 or L3
Active Power Total | Value (Hex) | 04 | 2B | xx | xx | xx | xx
| Description | DIF, 32 Bit Integer, 4 Byte | VIF, Active Power | Active Power Total
Reactive Power Phase L1, L2 and L3 | Value (Hex) | 84 | 80 | 40 | AB | FF | 0x | xx | xx | xx | xx
| Description | DIF, 32 Bit Integer, 4 Byte; Followed by a DIFE | DIFE, Total; Followed by a further DIFE | DIFE, Reactive Value | VIF, Reactive Power; Followed by a further VIFE | VIFE, Followed by an Manufacturer-spec.VIFE | Manufacturer-spec.VIFE: 01 : Phase L1 02 : Phase L2 03 : Phase L3 | Reactive Power Phase L1, L2 or L3
Reactive Power Total | Value (Hex) | 84 | 80 | 40 | 2B | xx | xx | xx | xx
| Description | DIF, 32 Bit Integer, 4 Byte; Followed by a DIFE | DIFE, Total; Followed by a further DIFE | DIFE, Reactive Value | VIF, Reactive Power | Reactive Power Total
Apparent Power Phase L1, L2 and L3 | Value (Hex) | 84 | C0 | 40 | AB | FF | 0x | xx | xx | xx | xx
| Description | DIF, 32 Bit Integer, 4 Byte; Followed by a DIFE | DIFE, Total; Followed by a further DIFE | DIFE, Apparent Value | VIF, Apparent Power; Followed by a further VIFE | VIFE, Followed by an Manufacturer-spec.VIFE | Manufacturer-spec.VIFE: 01 : Phase L1 02 : Phase L2 03 : Phase L3 | Apparent Power Phase L1, L2 or L3
Apparent Power Total | Value (Hex) | 84 | C0 | 40 | 2B | xx | xx | xx | xx
| Description | DIF, 32 Bit Integer, 4 Byte; Followed by a DIFE | DIFE, Total; Followed by a further DIFE | DIFE, Apparent Value | VIF, Apparent Power | Apparent Power Total
Voltage Phase L1, L2 and L3 | Value (Hex) | 02 | FD | C8 | FF | 0x | xx | xx
| Description | DIF, 16 Bit Integer, 2 Byte | VIF, Followed by a VIFE | VIFE = Voltage; Followed by a further VIFE | VIFE, Followed by an Manufacturer-spec.VIFE | Manufacturer-spec.VIFE: 01 : Phase L1 02 : Phase L2 03 : Phase L3 | Voltage Phase L1, L2 or L3
Voltage Total single Phase Meter | Value (Hex) | 02 | FD | 48 | xx | xx
| Description | DIF, 16 Bit Integer, 2 Byte | VIF, Followed by a VIFE | VIFE = Voltage | Voltage Total
Current Phase L1, L2 and L3 | Value (Hex) | 03 | FD | D9 | FF | 0x | xx | xx | xx
| Description | DIF, 23 Bit Integer, 3 Byte | VIF, Followed by a VIFE | VIFE = Current; Followed by a further VIFE | VIFE, Followed by an Manufacturer-spec.VIFE | Manufacturer-spec.VIFE: 01 : Phase L1 02 : Phase L2 03 : Phase L3 | Current Phase L1, L2 or L3
Current Total | Value (Hex) | 03 | FD | D9 | xx | xx | xx
| Description | DIF, 23 Bit Integer, 3 Byte | VIF, Followed by a VIFE | VIFE = Current Total | Current Total
Power factor cos phi Phase L1, L2 and L3 | Value (Hex) | 01 | FF | E1 | FF | 0x | xx
| Description | DIF, 8 Bit Integer, 1 Byte | VIF, Followed by an Manufacturer-spec.VIFE | Manufacturer-spec.VIFE = Power factor; Followed by a further VIFE | VIFE, Followed by an Manufacturer-spec.VIFE | Manufacturer-spec.VIFE: 01 : Phase L1 02 : Phase L2 03 : Phase L3 | Power factor cos phi Phase L1, L2 or L3
Power factor cos phi Total | Value (Hex) | 01 | FF | 61 | xx
| Description | DIF, 8 Bit Integer, 1 Byte | VIF, Followed by an Manufacturer-spec.VIFE | Manufacturer-spec.VIFE = Power factor cos phi | Power factor cos phi Total
Netfrequency | Value (Hex) | 02 | FF | 52 | xx | xx
| Description | DIF, 16 Bit Integer, 2 Byte | VIF, Followed by an Manufacturer-spec.VIFE | Manufacturer-spec.VIFE = Netfrequency | Netfrequency
Staus Byte 4 (Range Overflow) | Value (Hex) | 01 | FD | 17 | xx
| Description | DIF, 8 Bit Integer, 1 Byte | VIF, Followed by a VIFE | VIFE = Status (Error) Flags | Status Byte 4 (Range Overflow)
Tariff presently operating | Value (Hex) | 01 | FF | 13 | 0x
| Description | DIF, 8 Bit Integer, 1 Byte | VIF, Followed by an Manufacturer-spec.VIFE | Manufacturer-spec.VIFE = Tariff presently operating | Manufacturer-spec.VIFE: 01 : Phase L1 02 : Phase L2 03 : Phase L3

## Telegram of Error Flags
| Telegram of Error Flags | [9 empty] | Version 2.1
Telegram of Error Flags (REQ_UD1)
The Error Flags are transmitted by the M-Bus module within 35 – 75 ms from receipt of the Short Telegram „Transmit Error Flags“. Remark: The Error Flag and the M-Bus module Status on the Read-out Data Header are identical. The M-Bus module confirms correct receipt by Transmit the Error Flags. If there aren’t Error Flags set, the M-Bus module confirms correct receipt by Single Character Acknowledgement (ACK = E5). If the telegram was not correctly received the M-Bus module will not send an Acknowledgement.
Byte Nr.
|  | 1 | 2 | 3 |  |  | 4 | 5
Transmit Error Flags of M-Bus module | Value (Hex) | 10 | 7A | xx |  |  | xx | 16
| Description | Start Character Short Telegram | C- Field. Transmit Error Flags | A Field, Primary Address 00 – FA : Valid Primary Address FB, FC : Reserved for future use FD : Transmission using Secondary Address FE : All M-Bus module in the System send the Error Flags FF : No action by M-Bus module |  |  | CS Checksum, summed up from C-Field and A- Field | Stop Character
Byte Nr.
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
Telegram of Error Flags (RSP_UD) | Value (Hex) | 68 | 04 | 04 | 68 | 08 | xx | 71 | xx | xx | 16
| Description | Start Character Long- Telegram | L- Field | L- Field Repetition | Start Character Repetition | C- Field. Transmit Data from M-Bus module | A- Field, Primary Address (00 – FA = 0 – 250) | CI- Field, Error Flags of M-Bus module | Error Flags(1) | CS Checksum, summed up from C-Field to Error Flags inclusive | Stop Character
(1) Please see „Structure of Error Flags" “
The Error Flags are transmitted by the M-Bus module within 35 – 75 ms from receipt of the Short Telegram „Transmit Error Flags of M-Bus module“.
Remark: If there aren’t Error Flags set, the M-Bus module confirms correct receipt by Single Character Acknowledgement (ACK = E5).

## Structure of Error Flags
| Structure of Error Flags |  | Version 2.1
Structure of Error Flags Data Transmission from Meter to M-Bus module
The latest Data are transmitted every 4 seconds from the Meter to the M-Bus module. The Data Transmission from the Meter to the M-Bus module only works if the Meter is connected at least on one phase to the voltage system and the M-Bus module is connectet to the M-Bus Data Line. If the Voltage fails on the M-Bus the following Data are stored in an intermediary memory of an EEPROM: o Active or Reactive Energy Import Phase L1, L2, L3 and Total, Tariff 1 and Tariff 2. o Active or Reactive Energy Export Phase L1, L2, L3 and Total, Tariff 1 and Tariff 2. o Parameter Set of Read-out Data possible o Primary and Secondary Addresses for M-Bus Communication o Baud Rate for M-Bus Communication
Error Flag (Binär) | Error Flag (Hex Value) | Description
0000 xxxx | 0x | No Error has been set. => All instantaneous Data can be called via the M-Bus module.
0001 xxxx | 1x | The last Data Transmission from the Meter to the M-Bus module was faulty. The Meter is not connected to voltage or is faulty. => Only the Data of the last successful Data Transmission can be called via M-Bus module.
0011 xxxx | 3x | After putting the M-Bus module into operation no successful Data Transmission from the Meter to the M-Bus module has beeneffected. => The first Data Transmission is not yet completed (below 2 -6 sec.). => The Meter is not connected to system Voltage or is faulty. The M-Bus Data are not up-to-date. The Data are on „0“ or they correspond to the last Voltage failure.
Structure of Error Flags M-Bus module
The M-Bus module automatically carries out every second a number of internal tests, and, in the event of an Error, sets the corresponding Flag.
Error Flag (Binär) | Error Flag (Hex Value) | Description
xxxx 0000 | x0 | No Error set. => No Error in M-Bus module
xxxx 0001 | x1 | Error on Micro or Hardware fault.
xxxx 0010 | x2 | Overflow of internal Stack.
xxxx 0100 | x4 | Error on internal RAM (Memory Cell fault, etc..).
xxxx 1000 | x8 | Error on internal FLASH Memory.
xxxx 0011 | x3 | Error on Micro or Hardware fault and Overflow of internal Stack.
xxxx 0101 | x5 | Error on Micro or Hardware fault and Error on internal RAM.
xxxx 0110 | x6 | Overflow of internal Stack and Error on internal RAM.
xxxx 0111 | x7 | Error on Micro or Hardware fault and Overflow of internal Stack and Error on internal RAM.
xxxx 1001 | x9 | Error on Micro or Hardware fault and Error on internal FLASH Memory.
xxxx 1010 | xA | Overflow of internal Stack and Error on internal FLASH Memory.
xxxx 1011 | xB | Error on Micro or Hardware fault Overflow of internal Stack and Error on internal FLASH Memory.
xxxx 1100 | xC | Error on internal RAM and Error on internal FLASH Memory.
xxxx 1101 | xD | Error on Micro or Hardware fault and Error on internal RAM and Error on internal FLASH Memory.
xxxx 1110 | xE | Overflow of internal Stack and Error on internal RAM and Error on internal FLASH Memory.
xxxx 1111 | xF | Error on Micro or Hardware fault and Overflow of internal Stack and Error on internal RAM and Error on internal FLASH Memory.

## Initialisation of M-Bus
| Initialisation of M-Bus |  |  |  | Version 2.1
Initialisation of M-Bus module (SND_UD2)
This Short Telegram re-initialises the M-Bus module. The M-Bus module confirms correct receipt by Single Character Acknowledgement (ACK = E5). If the telegram was not correctly received the M-Bus module will not send an Acknowledgement.
Byte Nr.
|  | 1 | 2 | 3 | 4 | 5
Initialisation of M-Bus module | Value (Hex) | 10 | 40 | xx | xx | 16
| Description | Start Character Short Telegram | C- Field. REQ-UD2 | A Field, Primary Address 00 – FA : Valid Primary Address FB, FC : Reserved for future use FD : Transmission using Secondary Address FE : All M-Bus module in the System send the ACK FF : No action by M-Bus module | CS Checksum, summed up from C-Field and A- Field | Stop Character