## Device Identification
Device Identification
Product reference | [6 empty] | ECR180D ECR181D | ECA180D ECA181D | ECR380D ECR381D | ECA380D ECA381D | ECR310D ECR311D | ECA310D ECA311D | ECR300C ECR301C | ECA300C ECA301C | ECR180T | ECA180T
Description | Address DEC | Address HEX | Lengh (word) | Data Type | Function | 1P_40 | 1P_80 Modbus | 1P_80 Agardio | 3P_80 Modbus | 3P_80 Agardio | 3P_125 Modbus | 3P_125 Agardio | 3P_CT Modbus | 3P_CT Agardio | 3P_1P80 Modbus | 3P_1P80 Agardio
Vendor Name | 4096 | 1000 | 16 | STRING | H'03' | “Hager”
Product Code | 4112 | 1010 | 16 | STRING (1) | H'03' | ECR140D | ECR180D | ECA180D | ECR380D ECR381D | ECA380D ECA381D | ECR310D ECR311D | ECA310D ECA311D | ECR300C ECR301C | ECA300C ECA301C | ECR180T | ECA180T
SW version | 4128 | 1020 | 2 | (2) | H'03' | 0x02030000 (in this example, Firmware Version = 2.3.0)
Vendor URL | 4130 | 1022 | 16 | STRING | H'03' | “http://www.hager.com”
Product Name | 4146 | 1032 | 16 | STRING | H'03' | 1P_40 | 1P_80 Modbus | 1P_80 Agardio | 3P_80 Modbus | 3P_80 Agardio | 3P_125 Modbus | 3P_125 Aagrdio | 3P_CT Modbus | 3P_CT Agardio | 3P_1P80 Modbus | 3P_1P80 Agardio
Model Name | 4162 | 1042 | 16 | STRING | H'03' | “MODBUS Screw MID” | “MODBUS Screw MID” | “AGARDIO RJ45 MID” | “MODBUS Screw MID” | “AGARDIO RJ45 MID” | “MODBUS Screw MID” | “AGARDIO RJ45 MID” | “MODBUS Screw MID” | “AGARDIO RJ45 MID” | “MODBUS Screw” | “AGARDIO RJ45”
User Application Name | 4178 | 1052 | 16 | STRING | H'03' | "APL"
HW Version | 4194 | 1062 | 2 | (2) | H'03' | 0x04010000 (in this example, Hardware Version = 4.1.0)
Product code (Serial number) | 4196 | 1064 | 16 | (3) | H'03' | Example: 0318440021 : Ref.Id.=03 for ECR140D Year=2018 Week=44th Progr.N.=0021 | Example:0618440021 : Ref.Id.=06 for ECR180D Year=2018 Week=44th Progr.N.=0021 | Example: 0718440021 : Ref.Id.=07 for ECA180D Year=2018 Week=44th Progr.N.=0021 | Example: 3418440021 : Ref.Id.=34 for ECR380D Year=2018 Week=44th Progr.N.=0021 | Example: 3618440021 : Ref.Id.=36 for ECA380D Year=2018 Week=44th Progr.N.=0021 | Example: 4218440021 : Ref.Id.=42 for ECR310D Year=2018 Week=44th Progr.N.=0021 | Example: 4418440021 : Ref.Id.=44 for ECA310D Year=2018 Week=44th Progr.N.=0021 | Example: 5018440021 : Ref.Id.=50 for ECR300D Year=2018 Week=44th Progr.N.=0021 | Example: 5218440021 : Ref.Id.=52 for ECA300D Year=2018 Week=44th Progr.N.=0021 | Example: 2218440021 : Ref.Id.=22 for ECR180T Year=2018 Week=44th Progr.N.=0021 | Example: 2318440021 : Ref.Id.=23 for ECA180T Year=2018 Week=44th Progr.N.=0021
Product code (Site Code) | 4212 | 1074 | 2 | STRING | H'03' | "I" ("I" indicates Italy)
Production Date (Day of the Year) | 4214 | 1076 | 1 | U16 | H'03' | 213 (example, means 213th day of the Year)
Production Date (Year) | 4215 | 1077 | 1 | U16 | H'03' | 2018 (example)
(1) Chars sequence In case of Swiss market
(2) 3 levels version For example: 1.2.3 is coded 0x01020300 | [5 empty] | 21
In Strings data type values, chars are in sequence, with first char in MSByte. For example, “Hager “ in Vendor Name is in the following sequence:
Word 1: ‘H’ in Msbyte, ‘a’ in lsbyte Word2: ‘g’ in MSbyte, ‘e’ in lsbyte Word 3: ‘r’ in MSbyte, ‘/0‘ in lsbyte
the other words from 4 to 16 are full of blanks (\0, chr$(0))
Strings Swiss(*): these product codes are dedicated to those versions that do not show Reactive Energies on the display (Swiss market)

## Instantaneous Measures
Instantaneous Measures
Product reference | [7 empty] | ECR140D | ECR180D ECR181D ECA180D ECA181D | ECR380D ECR381D ECA380D ECA381D | ECR310D ECR311D ECA310D ECA311D | ECR300C ECR301C ECA300C ECA301C | ECR180T
Description | Unit | Resolution | Address DEC | Address HEX | Lengh (word) | Data Type | Function | 1P_40 | 1P_80 | 3P_80 | 3P_125 | 3P_CT | 3P_1P80 (*)
V(L1-N) | V | 0.01 | 45056 | B000 | 1 | U16 | H'03' | 9200…27600 | 9200…27600 | 9200…27600 | 9200…27600 | 9200…27600 | 9200…27600
V(L2-N) | V | 0.01 | 45057 | B001 | 1 | U16 | H'03' | 0xFFFF | 0xFFFF | 9200…27600 | 9200…27600 | 9200…27600 | 9200…27600
V(L3-N) | V | 0.01 | 45058 | B002 | 1 | U16 | H'03' | 0xFFFF | 0xFFFF | 9200…27600 | 9200…27600 | 9200…27600 | 9200…27600
V(L1-L2) | V | 0.01 | 45059 | B003 | 1 | U16 | H'03' | 0xFFFF | 0xFFFF | 16000…48000 | 16000…48000 | 16000…48000 | 0xFFFF
V(L2-L3) | V | 0.01 | 45060 | B004 | 1 | U16 | H'03' | 0xFFFF | 0xFFFF | 16000…48000 | 16000…48000 | 16000…48000 | 0xFFFF
V(L3-L1) | V | 0.01 | 45061 | B005 | 1 | U16 | H'03' | 0xFFFF | 0xFFFF | 16000…48000 | 16000…48000 | 16000…48000 | 0xFFFF
F | Hz | 0.01 | 45062 | B006 | 1 | U16 | H'03' | 4500…6500 | 4500…6500 | 4500…6500 | 4500…6500 | 4500…6500 | 4500…6500
Not Used | Hz | 0.01 | 45063 | B007 | 1 | U16 | H'03' | 0xFFFF | 0xFFFF | 0xFFFF | 0xFFFF | 0xFFFF | 0xFFFF
Not Used | Hz | 0.01 | 45064 | B008 | 1 | U16 | H'03' | 0xFFFF | 0xFFFF | 0xFFFF | 0xFFFF | 0xFFFF | 0xFFFF
I(L1) | mA | 1 | 45065 | B009 | 2 | U32 | H'03' | 0…40000 | 0…80000 | 0…80000 | 0…125000 | 0…7200000 | 0…80000
I(L2) | mA | 1 | 45067 | B00B | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0…80000 | 0…125000 | 0…7200000 | 0…80000
I(L3) | mA | 1 | 45069 | B00D | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0…80000 | 0…125000 | 0…7200000 | 0…80000
I(Neutral) | mA | 1 | 45071 | B00F | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0…80000 | 0…125000 | 0…7200000 | 0xFFFFFFFF
P(ΣL) | ±KW | 0.01 | 45073 | B011 | 2 | S32 | H'03' | -1104…+1104 | -2208…+2208 | -6624…+6624 | -10350…+10350 | -596160…+596160 | 0x7FFFFFFF
Q(ΣL) | ±kvar | 0.01 | 45075 | B013 | 2 | S32 | H'03' | -1104…+1104 | -2208…+2208 | -6624…+6624 | -10350…+10350 | -596160…+596160 | 0x7FFFFFFF
S(ΣL) | KvA | 0.01 | 45077 | B015 | 2 | U32 | H'03' | 0…1104 | 0…2208 | 0…6624 | 0…10350 | 0…596160 | 0xFFFFFFFF
PF(ΣL) IEC (§) |  | 0.001 | 45079 | B017 | 1 | S16 | H'03' | -1000…+1000 | -1000…+1000 | -1000…+1000 | -1000…+1000 | -1000…+1000 | 0x7FFF
PF(ΣL) IEEE (§) |  | 0.001 | 45080 | B018 | 1 | S16 | H'03' | -1000…+1000 | -1000…+1000 | -1000…+1000 | -1000…+1000 | -1000…+1000 | 0x7FFF
P(L1) | ±KW | 0.01 | 45081 | B019 | 2 | S32 | H'03' | -1104…+1104 | -2208…+2208 | -2208…+2208 | -3450…+3450 | -198720…+198720 | -2208…+2208
P(L2) | ±KW | 0.01 | 45083 | B01B | 2 | S32 | H'03' | 0x7FFFFFFF | 0x7FFFFFFF | -2208…+2208 | -3450…+3450 | -198720…+198720 | -2208…+2208
P(L3) | ±KW | 0.01 | 45085 | B01D | 2 | S32 | H'03' | 0x7FFFFFFF | 0x7FFFFFFF | -2208…+2208 | -3450…+3450 | -198720…+198720 | -2208…+2208
Q(L1) | ±kvar | 0.01 | 45087 | B01F | 2 | S32 | H'03' | -1104…+1104 | -2208…+2208 | -2208…+2208 | -3450…+3450 | -198720…+198720 | -2208…+2208
Q(L2) | ±kvar | 0.01 | 45089 | B021 | 2 | S32 | H'03' | 0x7FFFFFFF | 0x7FFFFFFF | -2208…+2208 | -3450…+3450 | -198720…+198720 | -2208…+2208
Q(L3) | ±kvar | 0.01 | 45091 | B023 | 2 | S32 | H'03' | 0x7FFFFFFF | 0x7FFFFFFF | -2208…+2208 | -3450…+3450 | -198720…+198720 | -2208…+2208
S(L1) | KvA | 0.01 | 45093 | B025 | 2 | U32 | H'03' | 0…1104 | 0…2208 | 0…2208 | 0…3450 | 0…198720 | 0…2208
S(L2) | KvA | 0.01 | 45095 | B027 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0…2208 | 0…3450 | 0…198720 | 0…2208
S(L3) | KvA | 0.01 | 45097 | B029 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0…2208 | 0…3450 | 0…198720 | 0…2208
PF(L1) IEC (§) |  | 0.001 | 45099 | B02B | 1 | S16 | H'03' | -1000…+1000 | -1000…+1000 | -1000…+1000 | -1000…+1000 | -1000…+1000 | -1000…+1000
PF(L2) IEC (§) |  | 0.001 | 45100 | B02C | 1 | S16 | H'03' | 0x7FFF | 0x7FFF | -1000…+1000 | -1000…+1000 | -1000…+1000 | -1000…+1000
PF(L3) IEC (§) |  | 0.001 | 45101 | B02D | 1 | S16 | H'03' | 0x7FFF | 0x7FFF | -1000…+1000 | -1000…+1000 | -1000…+1000 | -1000…+1000
PF(L1) IEEE (§) |  | 0.001 | 45102 | B02E | 1 | S16 | H'03' | -1000…+1000 | -1000…+1000 | -1000…+1000 | -1000…+1000 | -1000…+1000 | 0x7FFF
PF(L2) IEEE (§) |  | 0.001 | 45103 | B02F | 1 | S16 | H'03' | 0x7FFF | 0x7FFF | -1000…+1000 | -1000…+1000 | -1000…+1000 | 0x7FFF
PF(L3) IEEE (§) |  | 0.001 | 45104 | B030 | 1 | S16 | H'03' | 0x7FFF | 0x7FFF | -1000…+1000 | -1000…+1000 | -1000…+1000 | 0x7FFF
(*) in 3ple_1P_80A L1 means Meter 1, L2 means Meter2 and L3 means Meter3
(§) In case no power is flowing (Ln or ΣL), Power Factor is = +1000.

## Energies and partial Energies
Energies and partial Energies
Product reference | [7 empty] | ECR140D | ECR180D ECR181D ECA180D ECA181D | ECR380D ECR381D ECA380D ECA381D | ECR310D ECR311D ECA310D ECA311D | ECR300C ECR301C ECA300C ECA301C | ECR180T
Description | Unit | Resolution | Address DEC | Address HEX | Lengh (word) | Data Type | Function | 1P_40 | 1P_80 | 3P_80 | 3P_125 | 3P_CT | 3P_1P80
Ea+ (ΣT) | kWh | 1 | 45152 | B060 | 2 | U32 | H'03' | 0…99,999 | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Er+ (ΣT) | kvarh | 1 | 45154 | B062 | 2 | U32 | H'03' | 0…99,999 | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Ea- (ΣT) | kWh | 1 | 45156 | B064 | 2 | U32 | H'03' | 0…99,999 | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Er- (ΣT) | kvarh | 1 | 45158 | B066 | 2 | U32 | H'03' | 0…99,999 | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
P_Ea+ (ΣT) | kWh | 1 | 45160 | B068 | 2 | U32 | H'03' | 0xFFFFFFFF | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
P_Ea- (ΣT) | kWh | 1 | 45162 | B06A | 2 | U32 | H'03' | 0xFFFFFFFF | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Ea+ (M1)(ΣT) | kWh | 1 | 45184 | B080 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
Ea+ (M2)(ΣT) | kWh | 1 | 45186 | B082 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
Ea+ (M3)(ΣT) | kWh | 1 | 45188 | B084 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
Ea- (M1)(ΣT) | kWh | 1 | 45190 | B086 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
Ea- (M2)(ΣT) | kWh | 1 | 45192 | B088 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
Ea- (M3)(ΣT) | kWh | 1 | 45194 | B08A | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
P_Ea+ (M1)(ΣT) | kWh | 1 | 45196 | B08C | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
P_Ea+ (M2)(ΣT) | kWh | 1 | 45198 | B08E | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
P_Ea+ (M3)(ΣT) | kWh | 1 | 45200 | B090 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
P_Ea- (M1)(ΣT) | kWh | 1 | 45202 | B092 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
P_Ea- (M2)(ΣT) | kWh | 1 | 45204 | B094 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
P_Ea- (M3)(ΣT) | kWh | 1 | 45206 | B096 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999

## Tariff Control
Tariff Control
Product reference | [6 empty] | ECR140D | ECR180D ECR181D ECA180D ECA181D | ECR380D ECR381D ECA380D ECA381D | ECR310D ECR311D ECA310D ECA311D | ECR300C ECR301C ECA300C ECA301C | ECR180T
Description | Unit | Address DEC | Address HEX | Lengh (word) | Data Type | Function | 1P_40 | 1P_80 | 3P_80 | 3P_125 | 3P_CT | 3P_1P80
Number of available Tariffs = 8 (or 4) |  | 45232 | B0B0 | 1 | U16 | H'03' | Always = 8 (4 in 3ple_1P_80A)
Active Tariff on the product, regarding the Tariff Mode and physical input OR Modbus Tariff |  | 45233 | B0B1 | 1 | U16 | H'03' | 1…8 (1…4 in 3ple_1P_80A)
Physical Input Driven Tariff |  | 45234 | B0B2 | 1 | U16 | H'03' | 1…2 (0xFFFF in 1P_40 and 1P_80 Agardio, because they have no physical tariff digital input)
Tariff Mode: 0 or 1 (read only, can only be changed through HMI) |  | 45235 | B0B3 | 1 | U16 | H'03' | 0: tariff is HW driven (active tariff=Physical tariff) 1: tariff is Modbus driven (tariff by writing Set Tariff) (the tariff mode is defined by means of keyboard and display, except 1P_40 40 because it has no physical tariff digital input, hence Tariff_mode is always = 1)
Set Tariff (writable) (always read as 0) |  | 45236 | B0B4 | 1 | U16 | H'06' | 1…8 (1…4 in 3ple_1P_80A) writable (always read as 0)

## Energies per Tariff
Energies per Tariff
Product reference | [7 empty] | ECR140D | ECR180D ECR181D ECA180D ECA181D | ECR380D ECR381D ECA380D ECA381D | ECR310D ECR311D ECA310D ECA311D | ECR300C ECR301C ECA300C ECA301C | ECR180T
Description | Unit | Resolution | Address DEC | Address HEX | Lengh (word) | Data Type | Function | 1P_40 | 1P_80 | 3P_80 | 3P_125 | 3P_CT | 3P_1P80
Ea+ [T1] | kWh | 1 | 45248 | B0C0 | 2 | U32 | H'03' | 0…99,999 | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Ea+ [T2] | kWh | 1 | 45250 | B0C2 | 2 | U32 | H'03' | 0…99,999 | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Ea+ [T3] | kWh | 1 | 45252 | B0C4 | 2 | U32 | H'03' | 0…99,999 | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Ea+ [T4] | kWh | 1 | 45254 | B0C6 | 2 | U32 | H'03' | 0…99,999 | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Ea+ [T5] | kWh | 1 | 45256 | B0C8 | 2 | U32 | H'03' | 0…99,999 | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Ea+ [T6] | kWh | 1 | 45258 | B0CA | 2 | U32 | H'03' | 0…99,999 | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Ea+ [T7] | kWh | 1 | 45260 | B0CC | 2 | U32 | H'03' | 0…99,999 | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Ea+ [T8] | kWh | 1 | 45262 | B0CE | 2 | U32 | H'03' | 0…99,999 | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Ea- [T1] | kWh | 1 | 45264 | B0D0 | 2 | U32 | H'03' | 0…99,999 | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Ea- [T2] | kWh | 1 | 45266 | B0D2 | 2 | U32 | H'03' | 0…99,999 | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Ea- [T3] | kWh | 1 | 45268 | B0D4 | 2 | U32 | H'03' | 0…99,999 | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Ea- [T4] | kWh | 1 | 45270 | B0D6 | 2 | U32 | H'03' | 0…99,999 | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Ea- [T5] | kWh | 1 | 45272 | B0D8 | 2 | U32 | H'03' | 0…99,999 | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Ea- [T6] | kWh | 1 | 45274 | B0DA | 2 | U32 | H'03' | 0…99,999 | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Ea- [T7] | kWh | 1 | 45276 | B0DC | 2 | U32 | H'03' | 0…99,999 | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Ea- [T8] | kWh | 1 | 45278 | B0DE | 2 | U32 | H'03' | 0…99,999 | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Er+ [T1] | kvarh | 1 | 45280 | B0E0 | 2 | U32 | H'03' | 0…99,999 | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Er+ [T2] | kvarh | 1 | 45282 | B0E2 | 2 | U32 | H'03' | 0…99,999 | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Er+ [T3] | kvarh | 1 | 45284 | B0E4 | 2 | U32 | H'03' | 0…99,999 | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Er+ [T4] | kvarh | 1 | 45286 | B0E6 | 2 | U32 | H'03' | 0…99,999 | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Er+ [T5] | kvarh | 1 | 45288 | B0E8 | 2 | U32 | H'03' | 0…99,999 | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Er+ [T6] | kvarh | 1 | 45290 | B0EA | 2 | U32 | H'03' | 0…99,999 | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Er+ [T7] | kvarh | 1 | 45292 | B0EC | 2 | U32 | H'03' | 0…99,999 | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Er+ [T8] | kvarh | 1 | 45294 | B0EE | 2 | U32 | H'03' | 0…99,999 | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Er- [T1] | kvarh | 1 | 45296 | B0F0 | 2 | U32 | H'03' | 0…99,999 | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Er- [T2] | kvarh | 1 | 45298 | B0F2 | 2 | U32 | H'03' | 0…99,999 | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Er- [T3] | kvarh | 1 | 45300 | B0F4 | 2 | U32 | H'03' | 0…99,999 | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Er- [T4] | kvarh | 1 | 45302 | B0F6 | 2 | U32 | H'03' | 0…99,999 | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Er- [T5] | kvarh | 1 | 45304 | B0F8 | 2 | U32 | H'03' | 0…99,999 | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Er- [T6] | kvarh | 1 | 45306 | B0FA | 2 | U32 | H'03' | 0…99,999 | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Er- [T7] | kvarh | 1 | 45308 | B0FC | 2 | U32 | H'03' | 0…99,999 | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Er- [T8] | kvarh | 1 | 45310 | B0FE | 2 | U32 | H'03' | 0…99,999 | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Ea+ [M1] [T1] | kWh | 1 | 45488 | B1B0 | 2 | U33 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
Ea+ [M1] [T2] | kWh | 1 | 45490 | B1B2 | 2 | U34 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
Ea+ [M1] [T3] | kWh | 1 | 45492 | B1B4 | 2 | U35 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
Ea+ [M1] [T4] | kWh | 1 | 45494 | B1B6 | 2 | U36 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
Ea- [M1] [T1] | kWh | 1 | 45496 | B1B8 | 2 | U37 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
Ea- [M1] [T2] | kWh | 1 | 45498 | B1BA | 2 | U38 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
Ea- [M1] [T3] | kWh | 1 | 45500 | B1BC | 2 | U39 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
Ea- [M1] [T4] | kWh | 1 | 45502 | B1BE | 2 | U40 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
Ea+ [M2] [T1] | kWh | 1 | 45504 | B1C0 | 2 | U41 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
Ea+ [M2] [T2] | kWh | 1 | 45506 | B1C2 | 2 | U42 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
Ea+ [M2] [T3] | kWh | 1 | 45508 | B1C4 | 2 | U43 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
Ea+ [M2] [T4] | kWh | 1 | 45510 | B1C6 | 2 | U44 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
Ea- [M2] [T1] | kWh | 1 | 45512 | B1C8 | 2 | U45 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
Ea- [M2] [T2] | kWh | 1 | 45514 | B1CA | 2 | U46 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
Ea- [M2] [T3] | kWh | 1 | 45516 | B1CC | 2 | U47 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
Ea- [M2] [T4] | kWh | 1 | 45518 | B1CE | 2 | U48 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
Ea+ [M3] [T1] | kWh | 1 | 45520 | B1D0 | 2 | U49 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
Ea+ [M3] [T2] | kWh | 1 | 45522 | B1D2 | 2 | U50 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
Ea+ [M3] [T3] | kWh | 1 | 45524 | B1D4 | 2 | U51 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
Ea+ [M3] [T4] | kWh | 1 | 45526 | B1D6 | 2 | U52 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
Ea- [M3] [T1] | kWh | 1 | 45528 | B1D8 | 2 | U53 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
Ea- [M3] [T2] | kWh | 1 | 45530 | B1DA | 2 | U54 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
Ea- [M3] [T3] | kWh | 1 | 45532 | B1DC | 2 | U55 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
Ea- [M3] [T4] | kWh | 1 | 45534 | B1DE | 2 | U56 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999

## Partial Energie per Tariff
Partial Energie per Tariff
Product reference | [7 empty] | ECR140D | ECR180D ECR181D ECA180D ECA181D | ECR380D ECR381D ECA380D ECA381D | ECR310D ECR311D ECA310D ECA311D | ECR300C ECR301C ECA300C ECA301C | ECR180T
Description | Unit | Resolution | Address DEC | Address HEX | Lengh (word) | Data Type | Function | 1P_40 | 1P_80 | 3P_80 | 3P_125 | 3P_CT | 3P_1P80
P_Ea+ [T1] | kWh | 1 | 45376 | B140 | 2 | U32 | H'03' | 0xFFFFFFFF | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
P_Ea+ [T2] | kWh | 1 | 45378 | B142 | 2 | U32 | H'03' | 0xFFFFFFFF | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
P_Ea+ [T3] | kWh | 1 | 45380 | B144 | 2 | U32 | H'03' | 0xFFFFFFFF | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
P_Ea+ [T4] | kWh | 1 | 45382 | B146 | 2 | U32 | H'03' | 0xFFFFFFFF | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
P_Ea+ [T5] | kWh | 1 | 45384 | B148 | 2 | U32 | H'03' | 0xFFFFFFFF | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
P_Ea+ [T6] | kWh | 1 | 45386 | B14A | 2 | U32 | H'03' | 0xFFFFFFFF | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
P_Ea+ [T7] | kWh | 1 | 45388 | B14C | 2 | U32 | H'03' | 0xFFFFFFFF | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
P_Ea+ [T8] | kWh | 1 | 45390 | B14E | 2 | U32 | H'03' | 0xFFFFFFFF | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
P_Ea- [T1] | kWh | 1 | 45392 | B150 | 2 | U32 | H'03' | 0xFFFFFFFF | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
P_Ea- [T2] | kWh | 1 | 45394 | B152 | 2 | U32 | H'03' | 0xFFFFFFFF | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
P_Ea- [T3] | kWh | 1 | 45396 | B154 | 2 | U32 | H'03' | 0xFFFFFFFF | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
P_Ea- [T4] | kWh | 1 | 45398 | B156 | 2 | U32 | H'03' | 0xFFFFFFFF | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
P_Ea- [T5] | kWh | 1 | 45400 | B158 | 2 | U32 | H'03' | 0xFFFFFFFF | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
P_Ea- [T6] | kWh | 1 | 45402 | B15A | 2 | U32 | H'03' | 0xFFFFFFFF | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
P_Ea- [T7] | kWh | 1 | 45404 | B15C | 2 | U32 | H'03' | 0xFFFFFFFF | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
P_Ea- [T8] | kWh | 1 | 45406 | B15E | 2 | U32 | H'03' | 0xFFFFFFFF | 0…9,999,999 | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
P_Ea+ [M1] [T1] | kWh | 1 | 45584 | B210 | 2 | U33 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
P_Ea+ [M1] [T2] | kWh | 1 | 45586 | B212 | 2 | U34 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
P_Ea+ [M1] [T3] | kWh | 1 | 45588 | B214 | 2 | U35 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
P_Ea+ [M1] [T4] | kWh | 1 | 45590 | B216 | 2 | U36 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
P_Ea- [M1] [T1] | kWh | 1 | 45592 | B218 | 2 | U37 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
P_Ea- [M1] [T2] | kWh | 1 | 45594 | B21A | 2 | U38 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
P_Ea- [M1] [T3] | kWh | 1 | 45596 | B21C | 2 | U39 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
P_Ea- [M1] [T4] | kWh | 1 | 45598 | B21E | 2 | U40 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
P_Ea+ [M2] [T1] | kWh | 1 | 45600 | B220 | 2 | U41 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
P_Ea+ [M2] [T2] | kWh | 1 | 45602 | B222 | 2 | U42 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
P_Ea+ [M2] [T3] | kWh | 1 | 45604 | B224 | 2 | U43 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
P_Ea+ [M2] [T4] | kWh | 1 | 45606 | B226 | 2 | U44 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
P_Ea- [M2] [T1] | kWh | 1 | 45608 | B228 | 2 | U45 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
P_Ea- [M2] [T2] | kWh | 1 | 45610 | B22A | 2 | U46 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
P_Ea- [M2] [T3] | kWh | 1 | 45612 | B22C | 2 | U47 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
P_Ea- [M2] [T4] | kWh | 1 | 45614 | B22E | 2 | U48 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
P_Ea+ [M3] [T1] | kWh | 1 | 45616 | B230 | 2 | U49 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
P_Ea+ [M3] [T2] | kWh | 1 | 45618 | B232 | 2 | U50 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
P_Ea+ [M3] [T3] | kWh | 1 | 45620 | B234 | 2 | U51 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
P_Ea+ [M3] [T4] | kWh | 1 | 45622 | B236 | 2 | U52 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
P_Ea- [M3] [T1] | kWh | 1 | 45624 | B238 | 2 | U53 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
P_Ea- [M3] [T2] | kWh | 1 | 45626 | B23A | 2 | U54 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
P_Ea- [M3] [T3] | kWh | 1 | 45628 | B23C | 2 | U55 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999
P_Ea- [M3] [T4] | kWh | 1 | 45630 | B23E | 2 | U56 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999

## Energie per Phase
Energie per Phase
Product reference | [7 empty] | ECR140D | ECR180D ECR181D ECA180D ECA181D | ECR380D ECR381D ECA380D ECA381D | ECR310D ECR311D ECA310D ECA311D | ECR300C ECR301C ECA300C ECA301C | ECR180T
Description | Unit | Resolution | Address DEC | Address HEX | Lengh (word) | Data Type | Function | 1P_40 | 1P_80 | 3P_80 | 3P_125 | 3P_CT | 3P_1P80
Ea+[L1] | kWh | 1 | 45440 | B180 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Ea+[L2] | kWh | 1 | 45442 | B182 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Ea+[L3] | kWh | 1 | 45444 | B184 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Ea-[L1] | kWh | 1 | 45446 | B186 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Ea-[L2] | kWh | 1 | 45448 | B188 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Ea-[L3] | kWh | 1 | 45450 | B18A | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Er+[L1] | kvarh | 1 | 45452 | B18C | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Er+[L2] | kvarh | 1 | 45454 | B18E | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Er+[L3] | kvarh | 1 | 45456 | B190 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Er-[L1] | kvarh | 1 | 45458 | B192 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Er-[L2] | kvarh | 1 | 45460 | B194 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF
Er-[L3] | kvarh | 1 | 45462 | B196 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0…9,999,999 | 0…9,999,999 | 0…99,999,999 | 0xFFFFFFFF

## Instantaneous Measures S2
Instantaneous Measures Secondary
Product reference | [7 empty] | ECR140D | ECR180D ECR181D ECA180D ECA181D | ECR380D ECR381D ECA380D ECA381D | ECR310D ECR311D ECA310D ECA311D | ECR300C ECR301C ECA300C ECA301C | ECR180T
Description | Unit | Resolution | Address DEC | Address HEX | Lengh (word) | Data Type | Function | 1P_40 | 1P_80 | 3P_80 | 3P_125 | 3P_CT | 3P_1P80
V(L1-N) | V | 0.01 | 45680 | B270 | 1 | U16 | H'03' | 0xFFFF | 0xFFFF | 0xFFFF | 0xFFFF | 9200…27600 | 0xFFFF
V(L2-N) | V | 0.01 | 45681 | B271 | 1 | U16 | H'03' | 0xFFFF | 0xFFFF | 0xFFFF | 0xFFFF | 9200…27600 | 0xFFFF
V(L3-N) | V | 0.01 | 45682 | B272 | 1 | U16 | H'03' | 0xFFFF | 0xFFFF | 0xFFFF | 0xFFFF | 9200…27600 | 0xFFFF
V(L1-L2) | V | 0.01 | 45683 | B273 | 1 | U16 | H'03' | 0xFFFF | 0xFFFF | 0xFFFF | 0xFFFF | 16000…48000 | 0xFFFF
V(L2-L3) | V | 0.01 | 45684 | B274 | 1 | U16 | H'03' | 0xFFFF | 0xFFFF | 0xFFFF | 0xFFFF | 16000…48000 | 0xFFFF
V(L3-L1) | V | 0.01 | 45685 | B275 | 1 | U16 | H'03' | 0xFFFF | 0xFFFF | 0xFFFF | 0xFFFF | 16000…48000 | 0xFFFF
F | Hz | 0.01 | 45686 | B276 | 1 | U16 | H'03' | 0xFFFF | 0xFFFF | 0xFFFF | 0xFFFF | 4500…6500 | 0xFFFF
I(L1) | mA | 1 | 45687 | B277 | 1 | U16 | H'03' | 0xFFFF | 0xFFFF | 0xFFFF | 0xFFFF | 0…6000 | 0xFFFF
I(L2) | mA | 1 | 45688 | B278 | 1 | U16 | H'03' | 0xFFFF | 0xFFFF | 0xFFFF | 0xFFFF | 0…6000 | 0xFFFF
I(L3) | mA | 1 | 45689 | B279 | 1 | U16 | H'03' | 0xFFFF | 0xFFFF | 0xFFFF | 0xFFFF | 0…6000 | 0xFFFF
I(Neutral) | mA | 1 | 45690 | B27A | 1 | U16 | H'03' | 0xFFFF | 0xFFFF | 0xFFFF | 0xFFFF | 0…6000 | 0xFFFF
P(ΣL) | ±W | 1 | 45691 | B27B | 1 | U16 | H'03' | 0x7FFF | 0x7FFF | 0x7FFF | 0x7FFF | -4968…+4968 | 0x7FFF
Q(ΣL) | ±var | 1 | 45692 | B27C | 1 | U16 | H'03' | 0x7FFF | 0x7FFF | 0x7FFF | 0x7FFF | -4968…+4968 | 0x7FFF
S(ΣL) | VA | 1 | 45693 | B27D | 1 | U16 | H'03' | 0xFFFF | 0xFFFF | 0xFFFF | 0xFFFF | 0…4968 | 0xFFFF
PF(ΣL) IEC (§) |  | 0.001 | 45694 | B27E | 1 | U16 | H'03' | 0x7FFF | 0x7FFF | 0x7FFF | 0x7FFF | -1000…+1000 | 0x7FFF
PF(ΣL) IEEE (§) |  | 0.001 | 45695 | B27F | 1 | U16 | H'03' | 0x7FFF | 0x7FFF | 0x7FFF | 0x7FFF | -1000…+1000 | 0x7FFF
P(L1) | ±W | 1 | 45696 | B280 | 1 | U16 | H'03' | 0x7FFF | 0x7FFF | 0x7FFF | 0x7FFF | -1656…+1656 | 0x7FFF
P(L2) | ±W | 1 | 45697 | B281 | 1 | U16 | H'03' | 0x7FFF | 0x7FFF | 0x7FFF | 0x7FFF | -1656…+1656 | 0x7FFF
P(L3) | ±W | 1 | 45698 | B282 | 1 | U16 | H'03' | 0x7FFF | 0x7FFF | 0x7FFF | 0x7FFF | -1656…+1656 | 0x7FFF
Q(L1) | ±var | 1 | 45699 | B283 | 1 | U16 | H'03' | 0x7FFF | 0x7FFF | 0x7FFF | 0x7FFF | -1656…+1656 | 0x7FFF
Q(L2) | ±var | 1 | 45700 | B284 | 1 | U16 | H'03' | 0x7FFF | 0x7FFF | 0x7FFF | 0x7FFF | -1656…+1656 | 0x7FFF
Q(L3) | ±var | 1 | 45701 | B285 | 1 | U16 | H'03' | 0x7FFF | 0x7FFF | 0x7FFF | 0x7FFF | -1656…+1656 | 0x7FFF
S(L1) | VA | 1 | 45702 | B286 | 1 | U16 | H'03' | 0xFFFF | 0xFFFF | 0xFFFF | 0xFFFF | 0…1656 | 0xFFFF
S(L2) | VA | 1 | 45703 | B287 | 1 | U16 | H'03' | 0xFFFF | 0xFFFF | 0xFFFF | 0xFFFF | 0…1656 | 0xFFFF
S(L3) | VA | 1 | 45704 | B288 | 1 | U16 | H'03' | 0xFFFF | 0xFFFF | 0xFFFF | 0xFFFF | 0…1656 | 0xFFFF
PF(L1) IEC (§) |  | 0.001 | 45705 | B289 | 1 | U16 | H'03' | 0x7FFF | 0x7FFF | 0x7FFF | 0x7FFF | -1000…+1000 | 0x7FFF
PF(L2) IEC (§) |  | 0.001 | 45706 | B28A | 1 | U16 | H'03' | 0x7FFF | 0x7FFF | 0x7FFF | 0x7FFF | -1000…+1000 | 0x7FFF
PF(L3) IEC (§) |  | 0.001 | 45707 | B28B | 1 | U16 | H'03' | 0x7FFF | 0x7FFF | 0x7FFF | 0x7FFF | -1000…+1000 | 0x7FFF
PF(L1) IEEE (§) |  | 0.001 | 45708 | B28C | 1 | U16 | H'03' | 0x7FFF | 0x7FFF | 0x7FFF | 0x7FFF | -1000…+1000 | 0x7FFF
PF(L2) IEEE (§) |  | 0.001 | 45709 | B28D | 1 | U16 | H'03' | 0x7FFF | 0x7FFF | 0x7FFF | 0x7FFF | -1000…+1000 | 0x7FFF
PF(L3) IEEE (§) |  | 0.001 | 45710 | B28E | 1 | U16 | H'03' | 0x7FFF | 0x7FFF | 0x7FFF | 0x7FFF | -1000…+1000 | 0x7FFF

## Energies and Partial Energy S2
Energies and Partial Energy Secondary
Product reference | [7 empty] | ECR140D | ECR180D ECR181D ECA180D ECA181D | ECR380D ECR381D ECA380D ECA381D | ECR310D ECR311D ECA310D ECA311D | ECR300C ECR301C ECA300C ECA301C | ECR180T
Description | Unit | Resolution | Address DEC | Address HEX | Lengh (word) | Data Type | Function | 1P_40 | 1P_80 | 3P_80 | 3P_125 | 3P_CT | 3P_1P80
Ea+ (ΣT) | kWh | 0.01 | 45744 | B2B0 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
Er+ (ΣT) | kvarh | 0.01 | 45746 | B2B2 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
Ea- (ΣT) | kWh | 0.01 | 45748 | B2B4 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
Er- (ΣT) | kvarh | 0.01 | 45750 | B2B6 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
P_Ea+ (ΣT) | kWh | 0.01 | 45752 | B2B8 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
P_Ea- (ΣT) | kWh | 0.01 | 45754 | B2BA | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF

## Energies per tariff S2
Energies per tariff Secondary
Product reference | [7 empty] | ECR140D | ECR180D ECR181D ECA180D ECA181D | ECR380D ECR381D ECA380D ECA381D | ECR310D ECR311D ECA310D ECA311D | ECR300C ECR301C ECA300C ECA301C | ECR180T
Description | Unit | Resolution | Address DEC | Address HEX | Lengh (word) | Data Type | Function | 1P_40 | 1P_80 | 3P_80 | 3P_125 | 3P_CT | 3P_1P80
Ea+ [T1] | kWh | 0.01 | 45776 | B2D0 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
Ea+ [T2] | kWh | 0.01 | 45778 | B2D2 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
Ea+ [T3] | kWh | 0.01 | 45780 | B2D4 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
Ea+ [T4] | kWh | 0.01 | 45782 | B2D6 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
Ea+ [T5] | kWh | 0.01 | 45784 | B2D8 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
Ea+ [T6] | kWh | 0.01 | 45786 | B2DA | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
Ea+ [T7] | kWh | 0.01 | 45788 | B2DC | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
Ea+ [T8] | kWh | 0.01 | 45790 | B2DE | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
Ea- [T1] | kWh | 0.01 | 45792 | B2E0 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
Ea- [T2] | kWh | 0.01 | 45794 | B2E2 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
Ea- [T3] | kWh | 0.01 | 45796 | B2E4 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
Ea- [T4] | kWh | 0.01 | 45798 | B2E6 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
Ea- [T5] | kWh | 0.01 | 45800 | B2E8 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
Ea- [T6] | kWh | 0.01 | 45802 | B2EA | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
Ea- [T7] | kWh | 0.01 | 45804 | B2EC | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
Ea- [T8] | kWh | 0.01 | 45806 | B2EE | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
Er+ [T1] | kvarh | 0.01 | 45808 | B2F0 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
Er+ [T2] | kvarh | 0.01 | 45810 | B2F2 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
Er+ [T3] | kvarh | 0.01 | 45812 | B2F4 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
Er+ [T4] | kvarh | 0.01 | 45814 | B2F6 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
Er+ [T5] | kvarh | 0.01 | 45816 | B2F8 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
Er+ [T6] | kvarh | 0.01 | 45818 | B2FA | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
Er+ [T7] | kvarh | 0.01 | 45820 | B2FC | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
Er+ [T8] | kvarh | 0.01 | 45822 | B2FE | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
Er- [T1] | kvarh | 0.01 | 45824 | B300 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
Er- [T2] | kvarh | 0.01 | 45826 | B302 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
Er- [T3] | kvarh | 0.01 | 45828 | B304 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
Er- [T4] | kvarh | 0.01 | 45830 | B306 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
Er- [T5] | kvarh | 0.01 | 45832 | B308 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
Er- [T6] | kvarh | 0.01 | 45834 | B30A | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
Er- [T7] | kvarh | 0.01 | 45836 | B30C | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
Er- [T8] | kvarh | 0.01 | 45838 | B30E | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF

## Partial Energy per Tariff S2
Partial Energy per Tariff Secondary
Product reference | [7 empty] | ECR140D | ECR180D ECR181D ECA180D ECA181D | ECR380D ECR381D ECA380D ECA381D | ECR310D ECR311D ECA310D ECA311D | ECR300C ECR301C ECA300C ECA301C | ECR180T
Description | Unit | Resolution | Address DEC | Address HEX | Lengh (word) | Data Type | Function | 1P_40 | 1P_80 | 3P_80 | 3P_125 | 3P_CT | 3P_1P80
P_Ea+ [T1] | kWh | 0.01 | 45904 | B350 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
P_Ea+ [T2] | kWh | 0.01 | 45906 | B352 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
P_Ea+ [T3] | kWh | 0.01 | 45908 | B354 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
P_Ea+ [T4] | kWh | 0.01 | 45910 | B356 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
P_Ea+ [T5] | kWh | 0.01 | 45912 | B358 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
P_Ea+ [T6] | kWh | 0.01 | 45914 | B35A | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
P_Ea+ [T7] | kWh | 0.01 | 45916 | B35C | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
P_Ea+ [T8] | kWh | 0.01 | 45918 | B35E | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
P_Ea- [T1] | kWh | 0.01 | 45920 | B360 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
P_Ea- [T2] | kWh | 0.01 | 45922 | B362 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
P_Ea- [T3] | kWh | 0.01 | 45924 | B364 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
P_Ea- [T4] | kWh | 0.01 | 45926 | B366 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
P_Ea- [T5] | kWh | 0.01 | 45928 | B368 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
P_Ea- [T6] | kWh | 0.01 | 45930 | B36A | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
P_Ea- [T7] | kWh | 0.01 | 45932 | B36C | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
P_Ea- [T8] | kWh | 0.01 | 45934 | B36E | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF

## Energy per Phase S2
Energy per Phase Secondary
Product reference | [7 empty] | ECR140D | ECR180D ECR181D ECA180D ECA181D | ECR380D ECR381D ECA380D ECA381D | ECR310D ECR311D ECA310D ECA311D | ECR300C ECR301C ECA300C ECA301C | ECR180T
Description | Unit | Resolution | Address DEC | Address HEX | Lengh (word) | Data Type | Function | 1P_40 | 1P_80 | 3P_80 | 3P_125 | 3P_CT | 3P_1P80
Ea+ [L1] | kWh | 0.01 | 45968 | B390 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
Ea+ [L2] | kWh | 0.01 | 45970 | B392 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
Ea+ [L3] | kWh | 0.01 | 45972 | B394 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
Ea- [L1] | kWh | 0.01 | 45974 | B396 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
Ea- [L2] | kWh | 0.01 | 45976 | B398 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
Ea- [L3] | kWh | 0.01 | 45978 | B39A | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
Er+ [L1] | kvarh | 0.01 | 45980 | B39C | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
Er+ [L2] | kvarh | 0.01 | 45982 | B39E | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
Er+ [L3] | kvarh | 0.01 | 45984 | B3A0 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
Er- [L1] | kvarh | 0.01 | 45986 | B3A2 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
Er- [L2] | kvarh | 0.01 | 45988 | B3A4 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF
Er- [L3] | kvarh | 0.01 | 45990 | B3A6 | 2 | U32 | H'03' | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0xFFFFFFFF | 0…8,333,333 | 0xFFFFFFFF

## Network Settings
Network Settings
Product reference | [6 empty] | ECR140D | ECR180D ECR181D ECA180D ECA181D | ECR380D ECR381D ECA380D ECA381D | ECR310D ECR311D ECA310D ECA311D | ECR300C ECR301C ECA300C ECA301C | ECR180T
Description | Unit | Address DEC | Address HEX | Lengh (word) | Data Type | Function | 1P_40 | 1P_80 | 3P_80 | 3P_125 | 3P_CT | 3P_1P80
Network Type | enum | 49152 | C000 | 1 | U16 | H'03' | 1 : 1BL | 1 : 1BL | 4 : 4NBL | 4 : 4NBL | 4 : 4NBL | 1 : 1BL
CT secondary | A | 49153 | C001 | 1 | U16 | H'03' | 0xFFFF | 0xFFFF | 0xFFFF | 0xFFFF | 1 or 5 | 0xFFFF
CT primary | A | 49154 | C002 | 1 | U16 | H'03' | 0xFFFF | 0xFFFF | 0xFFFF | 0xFFFF | 1…1200 Or 5…6000 | 0xFFFF
MID Certified | enum | 49155 | C003 | 1 | U16 | H'03' | Always 1 =MID | Always 1 =MID | Always 1 =MID | Always 1 =MID | Always 1 =MID | Always 0=no MID

## Overflow Events
Overflow Events
Product reference | [6 empty] | ECR140D | ECR180D ECR181D ECA180D ECA181D | ECR380D ECR381D ECA380D ECA381D | ECR310D ECR311D ECA310D ECA311D | ECR300C ECR301C ECA300C ECA301C
Description | Unit | Address DEC | Address HEX | Lengh (word) | Data Type | Function | 1P_40 | 1P_80 | 3P_80 | 3P_125 | 3P_CT
Overflow value | kWh/kvarh | 49168 | C010 | 2 | U32 | H'03' | 100 | 10,000,000 | 10,000,000 | 10,000,000 | 83.333
Number of Overflow Events for Ea+ |  | 49170 | C012 | 1 | U16 | H'03' | 0…255 | 0…255 | 0…255 | 0…255 | 0…255
Number of Overflow Events for Er+ |  | 49171 | C013 | 1 | U16 | H'03' | 0…255 | 0…255 | 0…255 | 0…255 | 0…255
Number of Overflow Events for Ea- |  | 49172 | C014 | 1 | U16 | H'03' | 0…255 | 0…255 | 0…255 | 0…255 | 0…255
Number of Overflow Events for Er- |  | 49173 | C015 | 1 | U16 | H'03' | 0…255 | 0…255 | 0…255 | 0…255 | 0…255
Product reference | [11 empty] | ECR180T
Description | Unit | Address DEC | Address HEX | Lengh (word) | Data Type | Function | [5 empty] | 3P_1P80
Overflow value | kWh/kvarh | 49168 | C010 | 2 | U32 | H'03' | [5 empty] | 10,000,000
In the Most Significant byte: Number of Overflow Events for Ea+ [Meter1] In the Least Significant byte: Number of Overflow Events for Ea- [Meter1] |  | 49170 | C012 | 1 | U16 | H'03' | [5 empty] | MS byte 0…255 LS byte 0…255
In the Most Significant byte: Number of Overflow Events for Ea+ [Meter2] In the Least Significant byte: Number of Overflow Events for Ea- [Meter2] |  | 49171 | C013 | 1 | U16 | H'03' | [5 empty] | MS byte 0…255 LS byte 0…255
In the Most Significant byte: Number of Overflow Events for Ea+ [Meter3] In the Least Significant byte: Number of Overflow Events for Ea- [Meter3] |  | 49172 | C014 | 1 | U16 | H'03' | [5 empty] | MS byte 0…255 LS byte 0…255
|  | 49173 | C015 | 1 | U16 | [6 empty] | 0xFFFF

## Reset of Partial Energies
Reset of Partial Energies
Product reference | [6 empty] | ECR140D | ECR180D ECR181D ECA180D ECA181D | ECR380D ECR381D ECA380D ECA381D | ECR310D ECR311D ECA310D ECA311D | ECR300C ECR301C ECA300C ECA301C | ECR180T
Description | Unit | Address DEC | Address HEX | Lengh (word) | Data Type | Function | 1P_40 | 1P_80 | 3P_80 | 3P_125 | 3P_CT | 3P_1P80
Bit 0 clear all the Partial Registers of Tariff 1 |  | 49184 | C020 |  | U16 | H'03', H'06' | 0xFFFF | 0/1 | 0/1 | 0/1 | 0/1 | 0/1
Bit 1 clear all the Partial Registers of Tariff 2 |  | 49184 | C020 |  | U16 | H'03', H'06' | 0xFFFF | 0/1 | 0/1 | 0/1 | 0/1 | 0/1
Bit 2 clear all the Partial Registers of Tariff 3 |  | 49184 | C020 |  | U16 | H'03', H'06' | 0xFFFF | 0/1 | 0/1 | 0/1 | 0/1 | 0/1
Bit 3 clear all the Partial Registers of Tariff 4 |  | 49184 | C020 |  | U16 | H'03', H'06' | 0xFFFF | 0/1 | 0/1 | 0/1 | 0/1 | 0/1
Bit 4 clear all the Partial Registers of Tariff 5 |  | 49184 | C020 |  | U16 | H'03', H'06' | 0xFFFF | 0/1 | 0/1 | 0/1 | 0/1 | -
Bit 5 clear all the Partial Registers of Tariff 6 |  | 49184 | C020 |  | U16 | H'03', H'06' | 0xFFFF | 0/1 | 0/1 | 0/1 | 0/1 | -
Bit 6 clear all the Partial Registers of Tariff 7 |  | 49184 | C020 |  | U16 | H'03', H'06' | 0xFFFF | 0/1 | 0/1 | 0/1 | 0/1 | -
Bit 7 clear all the Partial Registers of Tariff 8 |  | 49184 | C020 |  | U16 | H'03', H'06' | 0xFFFF | 0/1 | 0/1 | 0/1 | 0/1 | -
Bit 0 clear the Partial Registers of Tariff 1 of Meter1 |  | 49185 | C021 |  | U16 | H'03', H'06' | 0xFFFF | 0/1 | 0/1 | 0/1 | 0/1 | 0xFFFF
Bit 1 clear the Partial Registers of Tariff 2 of Meter1 |  | 49185 | C021 |  | U16 | H'03', H'06' | 0xFFFF | 0/1 | 0/1 | 0/1 | 0/1 | 0xFFFF
Bit 2 clear the Partial Registers of Tariff 3 of Meter1 |  | 49185 | C021 |  | U16 | H'03', H'06' | 0xFFFF | 0/1 | 0/1 | 0/1 | 0/1 | 0xFFFF
Bit 3 clear the Partial Registers of Tariff 4 of Meter1 |  | 49185 | C021 |  | U16 | H'03', H'06' | 0xFFFF | 0/1 | 0/1 | 0/1 | 0/1 | 0xFFFF
Bit 0 clear the Partial Registers of Tariff 1 of Meter2 |  | 49186 | C022 |  | U16 | H'03', H'06' | 0xFFFF | 0/1 | 0/1 | 0/1 | 0/1 | 0xFFFF
Bit 1 clear the Partial Registers of Tariff 2 of Meter2 |  | 49186 | C022 |  | U16 | H'03', H'06' | 0xFFFF | 0/1 | 0/1 | 0/1 | 0/1 | 0xFFFF
Bit 2 clear the Partial Registers of Tariff 3 of Meter2 |  | 49186 | C022 |  | U16 | H'03', H'06' | 0xFFFF | 0/1 | 0/1 | 0/1 | 0/1 | 0xFFFF
Bit 3 clear the Partial Registers of Tariff 4 of Meter2 |  | 49186 | C022 |  | U16 | H'03', H'06' | 0xFFFF | 0/1 | 0/1 | 0/1 | 0/1 | 0xFFFF
Bit 0 clear the Partial Registers of Tariff 1 of Meter3 |  | 49187 | C023 |  | U16 | H'03', H'06' | 0xFFFF | 0/1 | 0/1 | 0/1 | 0/1 | 0xFFFF
Bit 1 clear the Partial Registers of Tariff 2 of Meter3 |  | 49187 | C023 |  | U16 | H'03', H'06' | 0xFFFF | 0/1 | 0/1 | 0/1 | 0/1 | 0xFFFF
Bit 2 clear the Partial Registers of Tariff 3 of Meter3 |  | 49187 | C023 |  | U16 | H'03', H'06' | 0xFFFF | 0/1 | 0/1 | 0/1 | 0/1 | 0xFFFF
Bit 3 clear the Partial Registers of Tariff 4 of Meter3 |  | 49187 | C023 |  | U16 | H'03', H'06' | 0xFFFF | 0/1 | 0/1 | 0/1 | 0/1 | 0xFFFF

## Debug Info
Debug Info
Product reference | [6 empty] | ECR140D | ECR180D ECR181D ECA180D ECA181D | ECR380D ECR381D ECA380D ECA381D | ECR310D ECR311D ECA310D ECA311D | ECR300C ECR301C ECA300C ECA301C | ECR180T
Description | Unit | Address DEC | Address HEX | Lengh (word) | Data Type | Function | 1P_40 | 1P_80 | 3P_80 | 3P_125 | 3P_CT | 3P_1P80
Number of device switch-on since its production |  | 49200 | C030 | 1 | U16 | H'03' | 1…999 | 1…999 | 1…999 | 1…999 | 1…999 | 1…999
Number of Buttons pushes |  | 49201 | C031 | 1 | U16 | H'03' | 1…9999 | 1…9999 | 1…9999 | 1…9999 | 1…9999 | 1…9999

## Modbus Configuration
Modbus Configuration
Product reference | [6 empty] | ECR140D | ECR180D ECR181D ECA180D ECA181D | ECR380D ECR381D ECA380D ECA381D | ECR310D ECR311D ECA310D ECA311D | ECR300C ECR301C ECA300C ECA301C | ECR180T
Description | Unit | Address DEC | Address HEX | Lengh (word) | Data Type | Function | 1P_40 | 1P_80 | 3P_80 | 3P_125 | 3P_CT | 3P_1P80
Modbus Address (writable) |  | 49216 | C040 | 1 | U16 | H'03' | 1…999 | 1…999 | 1…999 | 1…999 | 1…999 | 1…999
Modbus Baud Rate, Modbus Parity & Stop Bits (writable) |  | 49217 | C041 | 1 | U16 | H'03'
MSbyte = Baud Rate | Lsbyte = Parity
0x00 : 1200 | 0x00 = No Parity, 1 Stop Bit
0x01 : 2400 | 0x01 = No Parity, 2 Stop Bits
0x02 : 4800 | 0x02 = Odd Parity, 1 Stop Bit
0x03 : 9600 | 0x03 = Odd Parity, 2 Stop Bits
0x04 : 19200 | 0x04 = Even Parity, 1 Stop Bit
0x05 : 38400 | 0x05 = Even Parity, 2 Stop Bits
Examples:
0x0401 ß> 19200 baud, No Parity, 2 Stop Bits
0x0004 ß> 1200 baud, Even Parity, 1 Stop Bit

## Device Indentification Block
Device Identification
Product reference |  |  |  |  | ECR180D ECR181D | ECA180D ECA181D | ECR380D ECR381D | ECA380D ECA381D | ECR310D ECR311D | ECA310D ECA311D | ECR300C ECR301C | ECA300C ECA301C | ECR180T | ECA180T
Description | Object ID | Data Type | Function | 1P_40 | 1P_80 Modbus | 1P_80 Agardio | 3P_80 Modbus | 3P_80 Agardio | 3P_125 Modbus | 3P_125 Agardio | 3P_CT Modbus | 3P_CT Agardio | 3P_1P80 Modbus | 3P_1P80 Agardio
Vendor Name | 0x00 | ASCII | H'2B', H0E | “Hager”
Product Code In case of Swiss Mkt | 0x01 | ASCII | H'2B', H0E | ECR140D | ECR180D | ECA180D | ECR380D ECR381D | ECA380D ECA381D | ECR310D ECR311D | ECA310D ECA311D | ECR300C ECR301C | ECA300C ECA301C | ECR180T | ECA180T
Product Version | 0x02 | ASCII | H'2B', H0E | 0x02030000 (in this example, Firmware Version = 2.3.0)
Vendor URL | 0x03 | ASCII | H'2B', H0E | “http://www.hager.com”
Product Name | 0x04 | ASCII | H'2B', H0E | 1P_40 | 1P_80 Modbus | 1P_80 Agardio | 3P_80 Modbus | 3P_80 Agardio | 3P_125 Modbus | 3P_125 Aagrdio | 3P_CT Modbus | 3P_CT Agardio | 3P_1P80 Modbus | 3P_1P80 Agardio
Model Name | 0x05 | ASCII | H'2B', H0E | “MODBUS Screw MID” | “MODBUS Screw MID” | “AGARDIO RJ45 MID” | “MODBUS Screw MID” | “AGARDIO RJ45 MID” | “MODBUS Screw MID” | “AGARDIO RJ45 MID” | “MODBUS Screw MID” | “AGARDIO RJ45 MID” | “MODBUS Screw” | “AGARDIO RJ45”
User Application Name | 0x06 | ASCII | H'2B', H0E | "APL"
Serial | 0x80 | ASCII | H'2B', H0E | “0218230020” (example)
Production Date | 0x81 | ASCII | H'2B', H0E | “ddd/YYYY” (example = “143/2018”)
Hardware Version | 0x82 | ASCII | H'2B', H0E | “1.4.0” (example)
Applicable Functions: Read_Device_Identification (0x2B/0x0E)
User Blocks
Applicable Functions: User-Defined Functions (0x43/0x01, 0x43/0x02, 0x43/0x03)
Refer to “agardio.manager Slave Modbus Specification” Hager Group
Available Blocks: | 1
Maximum Words per Block: | 64