## Generalities
GENERALITIES
Generalities
The JBUS/MODBUS used by the product involves a dialogue using a master-slave hierarchical structure.
There are two possible dialogues :
- The master communicates with a slave and waits for its reply
- The master communicates with all the slaves without waiting for the reply
Hager products implement functions :
- 3 : to read n Words ( Maximum 125 words )
- 6 : to write 1 word
- 16 : to write n Word
The register type used are :
|  | long | 2 Words ( 4 bytes )
|  | int | 1 Word ( 2 Words )
If the register value is not available, according to its type and its signed, the indicated value is :
|  | unsigned long |  | FFFF FFFFhex
|  | signed long |  | 7FFF FFFF hex
|  | unsigned Int |  | FFFF hex
|  | signed int |  | 7FFF hex
Function 3 : Read n Words
Function 3 : Request frame format
Function 3 : Answer frame format
Number of Word asked in the Request frame
Data format is High and low order
Function 6 :Write 1 Word
Function 6 : Request frame format
When selecting slave address 0, the message is sent to all devices ( Hager or not ) present on the network ( No answer is sent by the device )
Function 6 : Answer frame format
Function 16 :Write n Words
Function 16 : Request frame format
When selecting slave address 0, the message is sent to all devices ( Hager or not ) present on the network : No answer is sent by the device
Function 16 : Answer frame format
1 Byte
0 < Value < 247

## Product Tables
Product name : SM103E
C550 Hex : Metrology Affected by current and voltage transformers
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function | Value if not Available
| 50512 | C550 | 2 | Hour Meter | 1/100 h | 3 | 0xFFFFFFFF
| 50514 | C552 | 2 | Phase to Phase Voltage: U12 | V/100 | 3 | 0xFFFFFFFF
| 50516 | C554 | 2 | Phase to Phase Voltage: U23 | V/100 | 3 | 0xFFFFFFFF
| 50518 | C556 | 2 | Phase to Phase Voltage: U31 | V/100 | 3 | 0xFFFFFFFF
| 50520 | C558 | 2 | Simple voltage : V1 | V/100 | 3 | 0xFFFFFFFF
| 50522 | C55A | 2 | Simple voltage : V2 | V/100 | 3 | 0xFFFFFFFF
| 50524 | C55C | 2 | Simple voltage : V3 | V/100 | 3 | 0xFFFFFFFF
| 50526 | C55E | 2 | Frequency : F | Hz/100 | 3 | 0xFFFFFFFF
| 50528 | C560 | 2 | Current : I1 | mA | 3 | 0xFFFFFFFF
| 50530 | C562 | 2 | Current : I2 | mA | 3 | 0xFFFFFFFF
| 50532 | C564 | 2 | Current : I3 | mA | 3 | 0xFFFFFFFF
| 50534 | C566 | 2 | Neutral Current : In | mA | 3 | 0xFFFFFFFF
| 50536 | C568 | 2 | ∑ Active Power +/- : P | kW/100 (Signed) | 3 | 0x7FFFFFFF
| 50538 | C56A | 2 | ∑ Reactive Power +/- : Q | kvar/100 (Signed) | 3 | 0x7FFFFFFF
| 50540 | C56C | 2 | ∑ Apparent Power : S | kVA/100 | 3 | 0xFFFFFFFF
| 50542 | C56E | 2 | ∑ Power Factor : -: leading et + : lagging : PF | 0,001 (Signed) | 3 | 0x7FFFFFFF
| 50544 | C570 | 2 | Active Power phase 1 +/- : P1 | kW/100 (Signed) | 3 | 0x7FFFFFFF
| 50546 | C572 | 2 | Active Power phase 2 +/- : P2 | kW/100 (Signed) | 3 | 0x7FFFFFFF
| 50548 | C574 | 2 | Active Power phase 3 +/- : P3 | kW/100 (Signed) | 3 | 0x7FFFFFFF
| 50550 | C576 | 2 | Reactive Power phase 1 +/- : Q1 | kvar/100 (Signed) | 3 | 0x7FFFFFFF
| 50552 | C578 | 2 | Reactive Power phase 2 +/- : Q2 | kvar/100 (Signed) | 3 | 0x7FFFFFFF
| 50554 | C57A | 2 | Reactive Power phase 3 +/- : Q3 | kvar/100 (Signed) | 3 | 0x7FFFFFFF
| 50556 | C57C | 2 | Apparent Power phase 1 : S1 | kVA/100 | 3 | 0xFFFFFFFF
| 50558 | C57E | 2 | Apparent Power phase 2 : S2 | kVA/100 | 3 | 0xFFFFFFFF
| 50560 | C580 | 2 | Apparent Power phase 3 : S3 | kVA/100 | 3 | 0xFFFFFFFF
| 50562 | C582 | 2 | Power Factor phase 1 -: leading and + : lagging : PF1 | 0,001 (Signed) | 3 | 0x7FFFFFFF
| 50564 | C584 | 2 | Power Factor phase 2 -: leading and + : lagging : PF2 | 0,001 (Signed) | 3 | 0x7FFFFFFF
| 50566 | C586 | 2 | Power Factor phase 3 -: leading and + : lagging : PF3 | 0,001 (Signed) | 3 | 0x7FFFFFFF
| 50568 | C588 | 2 | System value I Sys = ( I1+I2+I3) / 3 | mA | 3 | 0xFFFFFFFF
| 50570 | C58A | 2 | System value U Sys = (U12 + U23 + U31 ) / 3 | V/100 | 3 | 0xFFFFFFFF
| 50572 | C58C | 2 | System value V Sys = (V1 + V2 + V3 ) / 3 | V/100 | 3 | 0xFFFFFFFF
| 50512 | C550 | 62
C650 Hex : Energies
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function | Value if not Available
| 50768 | C650 | 2 | Hour meter | 1/100 h | 3 | 0xFFFFFFFF
| 50770 | C652 | 2 | Total Positive Active Energy (no resetable) : Ea+ | kWh | 3 | 0xFFFFFFFF
| 50772 | C654 | 2 | Total Positive Reactive Energy (no resetable) : Er + | kvarh | 3 | 0xFFFFFFFF
| 50774 | C656 | 2 | Total Apparent Energy (no resetable) : Es | kVAh | 3 | 0xFFFFFFFF
| 50776 | C658 | 2 | Total Negative Active Energy (no resetable) : Ea- | kWh | 3 | 0xFFFFFFFF
| 50778 | C65A | 2 | Total Negative Reactive Energy (no resetable) : Er - | kvarh | 3 | 0xFFFFFFFF
| 50780 | C65C | 2 | Total Positive Active Energy (resetable) : Ea+ | kWh | 3 | 0xFFFFFFFF
| 50782 | C65E | 2 | Total Positive Reactive Energy (resetable) : Er + | kvarh | 3 | 0xFFFFFFFF
| 50784 | C660 | 2 | Total Apparent Energy (resetable) : Es | kVAh | 3 | 0xFFFFFFFF
| 50786 | C662 | 2 | Total Negative Active Energy (resetable) : Ea- | kWh | 3 | 0xFFFFFFFF
| 50788 | C664 | 2 | Total Negative Reactive Energy (resetable) : Er - | kvarh | 3 | 0xFFFFFFFF
| 50790 | C666 | 2 | Number of pulse meter to read (6) | - | 3 | 0xFFFFFFFF
| 50792 | C668 | 2 | Total pulse meter Input 1 | - | 3 | 0xFFFFFFFF
| 50794 | C66A | 2 | Total pulse meter Input 2 | - | 3 | 0xFFFFFFFF
| 50796 | C66C | 2 | Total pulse meter Input 3 | - | 3 | 0xFFFFFFFF
| 50798 | C66E | 2 | Total pulse meter Input 4 | - | 3 | 0xFFFFFFFF
| 50800 | C670 | 2 | Total pulse meter Input 5 | - | 3 | 0xFFFFFFFF
| 50802 | C672 | 2 | Total pulse meter Input 6 | - | 3 | 0xFFFFFFFF
| 50804 | C674 | 2 | Total pulse meter Input 7 | - | 3 | 0xFFFFFFFF
| 50806 | C676 | 2 | Total pulse meter Input 8 | - | 3 | 0xFFFFFFFF
| 50808 | C678 | 2 | Total pulse meter Input 9 | - | 3 | 0xFFFFFFFF
| 50810 | C67A | 2 | Total pulse meter Input 10 | - | 3 | 0xFFFFFFFF
| 50812 | C67C | 2 | Predictive Active Power | kW | 3 | 0xFFFFFFFF
| 50814 | C67E | 2 | Predictive Reactive Power | kvar | 3 | 0xFFFFFFFF
| 50816 | C680 | 2 | Predictive Apparent Power | kVA | 3 | 0xFFFFFFFF
| 50818 | C682 | 2 | Mean positive active power between 2 signals | 0,01 kWh | 3 | 0xFFFFFFFF
| 50820 | C684 | 2 | Mean negative active power between 2 signals | 0,01 kWh | 3 | 0xFFFFFFFF
| 50822 | C686 | 2 | Mean positive reactive power between 2 signals | 0,01 kVARh | 3 | 0xFFFFFFFF
| 50824 | C688 | 2 | Mean negative reactive power between 2 signals | 0,01 kVARh | 3 | 0xFFFFFFFF
| 50826 | C68A | 2 | Last date for Record average P/Q/S in second since 01/01/2000 | s | 3 | 0xFFFFFFFF
| 50828 | C68C | 1 | Last average (P+) | W ( no affected by CT and VT ) | 3 | 0xFFFFFFFF
| 50829 | C68D | 1 | Last average (Q+) | var ( no affected by CT and VT ) | 3 | 0xFFFFFFFF
| 50830 | C68E | 1 | Last average (P-) | W ( no affected by CT and VT ) | 3 | 0xFFFFFFFF
| 50831 | C68F | 1 | Last average (Q-) | var ( no affected by CT and VT ) | 3 | 0xFFFFFFFF
| 50832 | C690 | 1 | Last average S | VA ( no affected by CT and VT ) | 3 | 0xFFFFFFFF
| 50768 | C650 | 65
C750 Hex : Statistique Affected by current and voltage transformers
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function | Value if not Available
| 51024 | C750 | 2 | Avg U12 | V/100 | 3 | 0xFFFFFFFF
| 51026 | C752 | 2 | Avg U23 | V/100 | 3 | 0xFFFFFFFF
| 51028 | C754 | 2 | Avg U31 | V/100 | 3 | 0xFFFFFFFF
| 51030 | C756 | 2 | Avg V1 | V/100 | 3 | 0xFFFFFFFF
| 51032 | C758 | 2 | Avg V2 | V/100 | 3 | 0xFFFFFFFF
| 51034 | C75A | 2 | Avg V3 | V/100 | 3 | 0xFFFFFFFF
| 51036 | C75C | 2 | Avg F | Hz/100 | 3 | 0xFFFFFFFF
| 51038 | C75E | 2 | Avg I1 | mA | 3 | 0xFFFFFFFF
| 51040 | C760 | 2 | Avg I2 | mA | 3 | 0xFFFFFFFF
| 51042 | C762 | 2 | Avg I3 | mA | 3 | 0xFFFFFFFF
| 51044 | C764 | 2 | Avg In | mA | 3 | 0xFFFFFFFF
| 51046 | C766 | 2 | Avg P+ (∑ active power +) | kW/100 | 3 | 0xFFFFFFFF
| 51048 | C768 | 2 | Avg P- (∑ active power -) | kW/100 | 3 | 0xFFFFFFFF
| 51050 | C76A | 2 | Avg Q+ (∑ reactive power +) | kvar/100 | 3 | 0xFFFFFFFF
| 51052 | C76C | 2 | Avg Q-(∑ reactive power -) | kvar/100 | 3 | 0xFFFFFFFF
| 51054 | C76E | 2 | Avg S (∑ apparent power) | kVA/100 | 3 | 0xFFFFFFFF
| 51056 | C770 | 2 | Max/avg U12 | V/100 | 3 | 0xFFFFFFFF
| 51058 | C772 | 2 | Max/avg U23 | V/100 | 3 | 0xFFFFFFFF
| 51060 | C774 | 2 | Max/avg U31 | V/100 | 3 | 0xFFFFFFFF
| 51062 | C776 | 2 | Max/avg V1 | V/100 | 3 | 0xFFFFFFFF
| 51064 | C778 | 2 | Max/avg V2 | V/100 | 3 | 0xFFFFFFFF
| 51066 | C77A | 2 | Max/avg V3 | V/100 | 3 | 0xFFFFFFFF
| 51068 | C77C | 2 | Max/avg F | Hz/100 | 3 | 0xFFFFFFFF
| 51070 | C77E | 2 | Max/avg I1 | mA | 3 | 0xFFFFFFFF
| 51072 | C780 | 2 | Max/avg I2 | mA | 3 | 0xFFFFFFFF
| 51074 | C782 | 2 | Max/avg I3 | mA | 3 | 0xFFFFFFFF
| 51076 | C784 | 2 | Max/avg In | mA | 3 | 0xFFFFFFFF
| 51078 | C786 | 2 | Max/avg P+ | kW/100 | 3 | 0xFFFFFFFF
| 51080 | C788 | 2 | Max/avg P- | kW/100 | 3 | 0xFFFFFFFF
| 51082 | C78A | 2 | Max/avg Q+ | kvar/100 | 3 | 0xFFFFFFFF
| 51084 | C78C | 2 | Max/avg Q- | kvar/100 | 3 | 0xFFFFFFFF
| 51086 | C78E | 2 | Max/avg S | kVA/100 | 3 | 0xFFFFFFFF
| 51088 | C790 | 1 | Minimum THD I | 0.1% | 3 | 0xFFFF
| 51089 | C791 | 1 | Minimum THD In | 0.1% | 3 | 0xFFFF
| 51090 | C792 | 1 | Minimum THD U | 0.1% | 3 | 0xFFFF
| 51091 | C793 | 1 | Maximum THD I | 0.1% | 3 | 0xFFFF
| 51092 | C794 | 1 | Maximum THD In | 0.1% | 3 | 0xFFFF
| 51093 | C795 | 1 | Maximum THD U | 0.1% | 3 | 0xFFFF
| 51024 | C750 | 70
C850 Hex : Metrology No Affected by current and voltage transformers
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function | Value if not Available
| 51280 | C850 | 1 | Hour Meter | h | 3 | 0xFFFF
| 51281 | C851 | 1 | Phase to Phase Voltage: U12 | V/100 | 3 | 0xFFFF
| 51282 | C852 | 1 | Phase to Phase Voltage: U23 | V/100 | 3 | 0xFFFF
| 51283 | C853 | 1 | Phase to Phase Voltage: U31 | V/100 | 3 | 0xFFFF
| 51284 | C854 | 1 | Simple voltage : V1 | V/100 | 3 | 0xFFFF
| 51285 | C855 | 1 | Simple voltage : V2 | V/100 | 3 | 0xFFFF
| 51286 | C856 | 1 | Simple voltage : V3 | V/100 | 3 | 0xFFFF
| 51287 | C857 | 1 | Frequency : F | Hz/100 | 3 | 0xFFFF
| 51288 | C858 | 1 | Current : I1 | mA | 3 | 0xFFFF
| 51289 | C859 | 1 | Current : I2 | mA | 3 | 0xFFFF
| 51290 | C85A | 1 | Current : I3 | mA | 3 | 0xFFFF
| 51291 | C85B | 1 | Neutral Current : In | mA | 3 | 0xFFFF
| 51292 | C85C | 1 | ∑ active Power +/- : P | kW/100 (Signed) | 3 | 0x7FFF
| 51293 | C85D | 1 | ∑ aeactive Power +/- : Q | kvar/100 (Signed) | 3 | 0x7FFF
| 51294 | C85E | 1 | ∑ apparent power : S | kVA/100 | 3 | 0xFFFF
| 51295 | C85F | 1 | ∑ power factor : -: leading and + : lagging : PF | 0,001 (Signed) | 3 | 0x7FFF
| 51296 | C860 | 1 | Active Power phase 1 +/- : P1 | kW/100 (Signed) | 3 | 0x7FFF
| 51297 | C861 | 1 | Active Power phase 2 +/- : P2 | kW/100 (Signed) | 3 | 0x7FFF
| 51298 | C862 | 1 | Active Power phase 3 +/- : P3 | kW/100 (Signed) | 3 | 0x7FFF
| 51299 | C863 | 1 | Reactive Power phase 1 +/- : Q1 | kvar/100 (Signed) | 3 | 0x7FFF
| 51300 | C864 | 1 | Reactive Power phase 2 +/- : Q2 | kvar/100 (Signed) | 3 | 0x7FFF
| 51301 | C865 | 1 | Reactive Power phase 3 +/- : Q3 | kvar/100 (Signed) | 3 | 0x7FFF
| 51302 | C866 | 1 | Apparent power phase 1 : S1 | kVA/100 | 3 | 0xFFFF
| 51303 | C867 | 1 | Apparent power phase 2 : S2 | kVA/100 | 3 | 0xFFFF
| 51304 | C868 | 1 | Apparent power phase 3 : S3 | kVA/100 | 3 | 0xFFFF
| 51305 | C869 | 1 | Power Factor phase 1 -: leading and + : lagging : PF1 | 0,001 (Signed) | 3 | 0x7FFF
| 51306 | C86A | 1 | Power Factor phase 2 -: leading and + : lagging : PF2 | 0,001 (Signed) | 3 | 0x7FFF
| 51307 | C86B | 1 | Power Factor phase 3 -: leading and + : lagging : PF3 | 0,001 (Signed) | 3 | 0x7FFF
| 51308 | C86C | 1 | System value I Sys = ( I1+I2+I3) / 3 | mA | 3 | 0xFFFF
| 51309 | C86D | 1 | System value U Sys = (U12 + U23 + U31 ) / 3 | V/100 | 3 | 0xFFFF
| 51310 | C86E | 1 | System value V Sys = (V1 + V2 + V3 ) / 3 | V/100 | 3 | 0xFFFF
| 51311 | C86F | 1 | Total Positive Active Energy (no resetable) : Ea+ | MWh | 3 | 0xFFFF
| 51312 | C870 | 1 | Total Positive Reactive Energy (no resetable) : Er + | Mvarh | 3 | 0xFFFF
| 51313 | C871 | 1 | Total Negative Active Energy (no resetable) : Ea- | MWh | 3 | 0xFFFF
| 51314 | C872 | 1 | Total Negative Reactive Energy (no resetable) : Er - | Mvarh | 3 | 0xFFFF
| 51280 | C850 | 35
C900 Hex : Temperatures
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 51456 | C900 | 1 | Internal module Temperature present | yes(1) / no (0) | 3
| 51457 | C901 | 1 | module Temperature | celsius degre | 3
| 51458 | C902 | 1 | Number of external Temperature sensors to read (from 0 to 5 max) | - | 3
| 51459 | C903 | 1 | Temperature extern 1 | celsius degre | 3
| 51460 | C904 | 1 | Temperature extern 2 | celsius degre | 3
| 51461 | C905 | 1 | Temperature extern 3 | celsius degre | 3
| 51462 | C906 | 1 | Temperature extern 4 | celsius degre | 3
| 51463 | C907 | 1 | Temperature extern 5 | celsius degre | 3
| 51456 | C900 | 8
C950 Hex : Harmonic
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function | Value if not Available
THD
| 51536 | C950 | 1 | thd U12 | 0.1% | 3 | 0XFFFF
| 51537 | C951 | 1 | thd U23 | 0.1% | 3 | 0XFFFF
| 51538 | C952 | 1 | thd U31 | 0.1% | 3 | 0XFFFF
| 51539 | C953 | 1 | thd V1 | 0.1% | 3 | 0XFFFF
| 51540 | C954 | 1 | thd V2 | 0.1% | 3 | 0XFFFF
| 51541 | C955 | 1 | thd V3 | 0.1% | 3 | 0XFFFF
| 51542 | C956 | 1 | thd I1 | 0.1% | 3 | 0XFFFF
| 51543 | C957 | 1 | thd I2 | 0.1% | 3 | 0XFFFF
| 51544 | C958 | 1 | thd I3 | 0.1% | 3 | 0XFFFF
| 51545 | C959 | 1 | thd In | 0.1% | 3 | 0XFFFF
| 51536 | C950 | 10
I : harmonic order
| 51546 | C95A | 1 | Number of harmonic rows |  | 3 | 0
| 51547 | C95B | 1 | harmonic I1 row 3 | 0.1% | 3 | 0XFFFF
| 51548 | C95C | 1 | harmonic I2 row 3 | 0.1% | 3 | 0XFFFF
| 51549 | C95D | 1 | harmonic I3 row 3 | 0.1% | 3 | 0XFFFF
| 51550 | C95E | 1 | harmonic IN row 3 | 0.1% | 3 | 0XFFFF
| 51551 | C95F | 1 | harmonic I1 row 5 | 0.1% | 3 | 0XFFFF
| 51552 | C960 | 1 | harmonic I2 row 5 | 0.1% | 3 | 0XFFFF
| 51553 | C961 | 1 | harmonic I3 row 5 | 0.1% | 3 | 0XFFFF
| 51554 | C962 | 1 | harmonic IN row 5 | 0.1% | 3 | 0XFFFF
| 51555 | C963 | 1 | harmonic I1 row 7 | 0.1% | 3 | 0XFFFF
| 51556 | C964 | 1 | harmonic I2 row 7 | 0.1% | 3 | 0XFFFF
| 51557 | C965 | 1 | harmonic I3 row 7 | 0.1% | 3 | 0XFFFF
| 51558 | C966 | 1 | harmonic IN row 7 | 0.1% | 3 | 0XFFFF
| 51559 | C967 | 1 | harmonic I1 row 9 | 0.1% | 3 | 0XFFFF
| 51560 | C968 | 1 | harmonic I2 row 9 | 0.1% | 3 | 0XFFFF
| 51561 | C969 | 1 | harmonic I3 row 9 | 0.1% | 3 | 0XFFFF
| 51562 | C96A | 1 | harmonic IN row 9 | 0.1% | 3 | 0XFFFF
| 51563 | C96B | 1 | harmonic I1 row 11 | 0.1% | 3 | 0XFFFF
| 51564 | C96C | 1 | harmonic I2 row 11 | 0.1% | 3 | 0XFFFF
| 51565 | C96D | 1 | harmonic I3 row 11 | 0.1% | 3 | 0XFFFF
| 51566 | C96E | 1 | harmonic IN row 11 | 0.1% | 3 | 0XFFFF
| 51567 | C96F | 1 | harmonic I1 row 13 | 0.1% | 3 | 0XFFFF
| 51568 | C970 | 1 | harmonic I2 row 13 | 0.1% | 3 | 0XFFFF
| 51569 | C971 | 1 | harmonic I3 row 13 | 0.1% | 3 | 0XFFFF
| 51570 | C972 | 1 | harmonic IN row 13 | 0.1% | 3 | 0XFFFF
| 51571 | C973 | 1 | harmonic I1 row 15 | 0.1% | 3 | 0XFFFF
| 51572 | C974 | 1 | harmonic I2 row 15 | 0.1% | 3 | 0XFFFF
| 51573 | C975 | 1 | harmonic I3 row 15 | 0.1% | 3 | 0XFFFF
| 51574 | C976 | 1 | harmonic IN row 15 | 0.1% | 3 | 0XFFFF
| 51575 | C977 | 1 | harmonic I1 row 17 | 0.1% | 3 | 0XFFFF
| 51576 | C978 | 1 | harmonic I2 row 17 | 0.1% | 3 | 0XFFFF
| 51577 | C979 | 1 | harmonic I3 row 17 | 0.1% | 3 | 0XFFFF
| 51578 | C97A | 1 | harmonic IN row 17 | 0.1% | 3 | 0XFFFF
| 51579 | C97B | 1 | harmonic I1 row 19 | 0.1% | 3 | 0XFFFF
| 51580 | C97C | 1 | harmonic I2 row 19 | 0.1% | 3 | 0XFFFF
| 51581 | C97D | 1 | harmonic I3 row 19 | 0.1% | 3 | 0XFFFF
| 51582 | C97E | 1 | harmonic IN row 19 | 0.1% | 3 | 0XFFFF
| 51583 | C97F | 1 | harmonic I1 row 21 | 0.1% | 3 | 0XFFFF
| 51584 | C980 | 1 | harmonic I2 row 21 | 0.1% | 3 | 0XFFFF
| 51585 | C981 | 1 | harmonic I3 row 21 | 0.1% | 3 | 0XFFFF
| 51586 | C982 | 1 | harmonic IN row 21 | 0.1% | 3 | 0XFFFF
| 51587 | C983 | 1 | harmonic I1 row 23 | 0.1% | 3 | 0XFFFF
| 51588 | C984 | 1 | harmonic I2 row 23 | 0.1% | 3 | 0XFFFF
| 51589 | C985 | 1 | harmonic I3 row 23 | 0.1% | 3 | 0XFFFF
| 51590 | C986 | 1 | harmonic IN row 23 | 0.1% | 3 | 0XFFFF
| 51591 | C987 | 1 | harmonic I1 row 25 | 0.1% | 3 | 0XFFFF
| 51592 | C988 | 1 | harmonic I2 row 25 | 0.1% | 3 | 0XFFFF
| 51593 | C989 | 1 | harmonic I3 row 25 | 0.1% | 3 | 0XFFFF
| 51594 | C98A | 1 | harmonic IN row 25 | 0.1% | 3 | 0XFFFF
| 51595 | C98B | 1 | harmonic I1 row 27 | 0.1% | 3 | 0XFFFF
| 51596 | C98C | 1 | harmonic I2 row 27 | 0.1% | 3 | 0XFFFF
| 51597 | C98D | 1 | harmonic I3 row 27 | 0.1% | 3 | 0XFFFF
| 51598 | C98E | 1 | harmonic IN row 27 | 0.1% | 3 | 0XFFFF
| 51599 | C98F | 1 | harmonic I1 row 29 | 0.1% | 3 | 0XFFFF
| 51600 | C990 | 1 | harmonic I2 row 29 | 0.1% | 3 | 0XFFFF
| 51601 | C991 | 1 | harmonic I3 row 29 | 0.1% | 3 | 0XFFFF
| 51602 | C992 | 1 | harmonic IN row 29 | 0.1% | 3 | 0XFFFF
| 51603 | C993 | 1 | harmonic I1 row 31 | 0.1% | 3 | 0XFFFF
| 51604 | C994 | 1 | harmonic I2 row 31 | 0.1% | 3 | 0XFFFF
| 51605 | C995 | 1 | harmonic I3 row 31 | 0.1% | 3 | 0XFFFF
| 51606 | C996 | 1 | harmonic IN row 31 | 0.1% | 3 | 0XFFFF
| 51607 | C997 | 1 | harmonic I1 row 33 | 0.1% | 3 | 0XFFFF
| 51608 | C998 | 1 | harmonic I2 row 33 | 0.1% | 3 | 0XFFFF
| 51609 | C999 | 1 | harmonic I3 row 33 | 0.1% | 3 | 0XFFFF
| 51610 | C99A | 1 | harmonic IN row 33 | 0.1% | 3 | 0XFFFF
| 51611 | C99B | 1 | harmonic I1 row 35 | 0.1% | 3 | 0XFFFF
| 51612 | C99C | 1 | harmonic I2 row 35 | 0.1% | 3 | 0XFFFF
| 51613 | C99D | 1 | harmonic I3 row 35 | 0.1% | 3 | 0XFFFF
| 51614 | C99E | 1 | harmonic IN row 35 | 0.1% | 3 | 0XFFFF
| 51615 | C99F | 1 | harmonic I1 row 37 | 0.1% | 3 | 0XFFFF
| 51616 | C9A0 | 1 | harmonic I2 row 37 | 0.1% | 3 | 0XFFFF
| 51617 | C9A1 | 1 | harmonic I3 row 37 | 0.1% | 3 | 0XFFFF
| 51618 | C9A2 | 1 | harmonic IN row 37 | 0.1% | 3 | 0XFFFF
| 51619 | C9A3 | 1 | harmonic I1 row 39 | 0.1% | 3 | 0XFFFF
| 51620 | C9A4 | 1 | harmonic I2 row 39 | 0.1% | 3 | 0XFFFF
| 51621 | C9A5 | 1 | harmonic I3 row 39 | 0.1% | 3 | 0XFFFF
| 51622 | C9A6 | 1 | harmonic IN row 39 | 0.1% | 3 | 0XFFFF
| 51623 | C9A7 | 1 | harmonic I1 row 41 | 0.1% | 3 | 0XFFFF
| 51624 | C9A8 | 1 | harmonic I2 row 41 | 0.1% | 3 | 0XFFFF
| 51625 | C9A9 | 1 | harmonic I3 row 41 | 0.1% | 3 | 0XFFFF
| 51626 | C9AA | 1 | harmonic IN row 41 | 0.1% | 3 | 0XFFFF
| 51627 | C9AB | 1 | harmonic I1 row 43 | 0.1% | 3 | 0XFFFF
| 51628 | C9AC | 1 | harmonic I2 row 43 | 0.1% | 3 | 0XFFFF
| 51629 | C9AD | 1 | harmonic I3 row 43 | 0.1% | 3 | 0XFFFF
| 51630 | C9AE | 1 | harmonic IN row 43 | 0.1% | 3 | 0XFFFF
| 51631 | C9AF | 1 | harmonic I1 row 45 | 0.1% | 3 | 0XFFFF
| 51632 | C9B0 | 1 | harmonic I2 row 45 | 0.1% | 3 | 0XFFFF
| 51633 | C9B1 | 1 | harmonic I3 row 45 | 0.1% | 3 | 0XFFFF
| 51634 | C9B2 | 1 | harmonic IN row 45 | 0.1% | 3 | 0XFFFF
| 51635 | C9B3 | 1 | harmonic I1 row 47 | 0.1% | 3 | 0XFFFF
| 51636 | C9B4 | 1 | harmonic I2 row 47 | 0.1% | 3 | 0XFFFF
| 51637 | C9B5 | 1 | harmonic I3 row 47 | 0.1% | 3 | 0XFFFF
| 51638 | C9B6 | 1 | harmonic IN row 47 | 0.1% | 3 | 0XFFFF
| 51639 | C9B7 | 1 | harmonic I1 row 49 | 0.1% | 3 | 0XFFFF
| 51640 | C9B8 | 1 | harmonic I2 row 49 | 0.1% | 3 | 0XFFFF
| 51641 | C9B9 | 1 | harmonic I3 row 49 | 0.1% | 3 | 0XFFFF
| 51642 | C9BA | 1 | harmonic IN row 49 | 0.1% | 3 | 0XFFFF
| 51643 | C9BB | 1 | harmonic I1 row 51 | 0.1% | 3 | 0XFFFF
| 51644 | C9BC | 1 | harmonic I2 row 51 | 0.1% | 3 | 0XFFFF
| 51645 | C9BD | 1 | harmonic I3 row 51 | 0.1% | 3 | 0XFFFF
| 51646 | C9BE | 1 | harmonic IN row 51 | 0.1% | 3 | 0XFFFF
| 51647 | C9BF | 1 | harmonic I1 row 53 | 0.1% | 3 | 0XFFFF
| 51648 | C9C0 | 1 | harmonic I2 row 53 | 0.1% | 3 | 0XFFFF
| 51649 | C9C1 | 1 | harmonic I3 row 53 | 0.1% | 3 | 0XFFFF
| 51650 | C9C2 | 1 | harmonic IN row 53 | 0.1% | 3 | 0XFFFF
| 51651 | C9C3 | 1 | harmonic I1 row 55 | 0.1% | 3 | 0XFFFF
| 51652 | C9C4 | 1 | harmonic I2 row 55 | 0.1% | 3 | 0XFFFF
| 51653 | C9C5 | 1 | harmonic I3 row 55 | 0.1% | 3 | 0XFFFF
| 51654 | C9C6 | 1 | harmonic IN row 55 | 0.1% | 3 | 0XFFFF
| 51655 | C9C7 | 1 | harmonic I1 row 57 | 0.1% | 3 | 0XFFFF
| 51656 | C9C8 | 1 | harmonic I2 row 57 | 0.1% | 3 | 0XFFFF
| 51657 | C9C9 | 1 | harmonic I3 row 57 | 0.1% | 3 | 0XFFFF
| 51658 | C9CA | 1 | harmonic IN row 57 | 0.1% | 3 | 0XFFFF
| 51659 | C9CB | 1 | harmonic I1 row 59 | 0.1% | 3 | 0XFFFF
| 51660 | C9CC | 1 | harmonic I2 row 59 | 0.1% | 3 | 0XFFFF
| 51661 | C9CD | 1 | harmonic I3 row 59 | 0.1% | 3 | 0XFFFF
| 51662 | C9CE | 1 | harmonic IN row 59 | 0.1% | 3 | 0XFFFF
| 51663 | C9CF | 1 | harmonic I1 row 61 | 0.1% | 3 | 0XFFFF
| 51664 | C9D0 | 1 | harmonic I2 row 61 | 0.1% | 3 | 0XFFFF
| 51665 | C9D1 | 1 | harmonic I3 row 61 | 0.1% | 3 | 0XFFFF
| 51666 | C9D2 | 1 | harmonic IN row 61 | 0.1% | 3 | 0XFFFF
| 51667 | C9D3 | 1 | harmonic I1 row 63 | 0.1% | 3 | 0XFFFF
| 51668 | C9D4 | 1 | harmonic I2 row 63 | 0.1% | 3 | 0XFFFF
| 51669 | C9D5 | 1 | harmonic I3 row 63 | 0.1% | 3 | 0XFFFF
| 51670 | C9D6 | 1 | harmonic IN row 63 | 0.1% | 3 | 0XFFFF
| 51546 | C95A | 125
V PH/Ph :harmonic order
| 51671 | C9D7 | 1 | Number of harmonic rows |  | 3 | 0
| 51672 | C9D8 | 1 | harmonic U12 row 3 | 0.1% | 3 | 0XFFFF
| 51673 | C9D9 | 1 | harmonic U23 row 3 | 0.1% | 3 | 0XFFFF
| 51674 | C9DA | 1 | harmonic U31 row 3 | 0.1% | 3 | 0XFFFF
| 51675 | C9DB | 1 | harmonic U12 row 5 | 0.1% | 3 | 0XFFFF
| 51676 | C9DC | 1 | harmonic U23 row 5 | 0.1% | 3 | 0XFFFF
| 51677 | C9DD | 1 | harmonic U31 row 5 | 0.1% | 3 | 0XFFFF
| 51678 | C9DE | 1 | harmonic U12 row 7 | 0.1% | 3 | 0XFFFF
| 51679 | C9DF | 1 | harmonic U23 row 7 | 0.1% | 3 | 0XFFFF
| 51680 | C9E0 | 1 | harmonic U31 row 7 | 0.1% | 3 | 0XFFFF
| 51681 | C9E1 | 1 | harmonic U12 row 9 | 0.1% | 3 | 0XFFFF
| 51682 | C9E2 | 1 | harmonic U23 row 9 | 0.1% | 3 | 0XFFFF
| 51683 | C9E3 | 1 | harmonic U31 row 9 | 0.1% | 3 | 0XFFFF
| 51684 | C9E4 | 1 | harmonic U12 row 11 | 0.1% | 3 | 0XFFFF
| 51685 | C9E5 | 1 | harmonic U23 row 11 | 0.1% | 3 | 0XFFFF
| 51686 | C9E6 | 1 | harmonic U31 row 11 | 0.1% | 3 | 0XFFFF
| 51687 | C9E7 | 1 | harmonic U12 row 13 | 0.1% | 3 | 0XFFFF
| 51688 | C9E8 | 1 | harmonic U23 row 13 | 0.1% | 3 | 0XFFFF
| 51689 | C9E9 | 1 | harmonic U31 row 13 | 0.1% | 3 | 0XFFFF
| 51690 | C9EA | 1 | harmonic U12 row 15 | 0.1% | 3 | 0XFFFF
| 51691 | C9EB | 1 | harmonic U23 row 15 | 0.1% | 3 | 0XFFFF
| 51692 | C9EC | 1 | harmonic U31 row 15 | 0.1% | 3 | 0XFFFF
| 51693 | C9ED | 1 | harmonic U12 row 17 | 0.1% | 3 | 0XFFFF
| 51694 | C9EE | 1 | harmonic U23 row 17 | 0.1% | 3 | 0XFFFF
| 51695 | C9EF | 1 | harmonic U31 row 17 | 0.1% | 3 | 0XFFFF
| 51696 | C9F0 | 1 | harmonic U12 row 19 | 0.1% | 3 | 0XFFFF
| 51697 | C9F1 | 1 | harmonic U23 row 19 | 0.1% | 3 | 0XFFFF
| 51698 | C9F2 | 1 | harmonic U31 row 19 | 0.1% | 3 | 0XFFFF
| 51699 | C9F3 | 1 | harmonic U12 row 21 | 0.1% | 3 | 0XFFFF
| 51700 | C9F4 | 1 | harmonic U23 row 21 | 0.1% | 3 | 0XFFFF
| 51701 | C9F5 | 1 | harmonic U31 row 21 | 0.1% | 3 | 0XFFFF
| 51702 | C9F6 | 1 | harmonic U12 row 23 | 0.1% | 3 | 0XFFFF
| 51703 | C9F7 | 1 | harmonic U23 row 23 | 0.1% | 3 | 0XFFFF
| 51704 | C9F8 | 1 | harmonic U31 row 23 | 0.1% | 3 | 0XFFFF
| 51705 | C9F9 | 1 | harmonic U12 row 25 | 0.1% | 3 | 0XFFFF
| 51706 | C9FA | 1 | harmonic U23 row 25 | 0.1% | 3 | 0XFFFF
| 51707 | C9FB | 1 | harmonic U31 row 25 | 0.1% | 3 | 0XFFFF
| 51708 | C9FC | 1 | harmonic U12 row 27 | 0.1% | 3 | 0XFFFF
| 51709 | C9FD | 1 | harmonic U23 row 27 | 0.1% | 3 | 0XFFFF
| 51710 | C9FE | 1 | harmonic U31 row 27 | 0.1% | 3 | 0XFFFF
| 51711 | C9FF | 1 | harmonic U12 row 29 | 0.1% | 3 | 0XFFFF
| 51712 | CA00 | 1 | harmonic U23 row 29 | 0.1% | 3 | 0XFFFF
| 51713 | CA01 | 1 | harmonic U31 row 29 | 0.1% | 3 | 0XFFFF
| 51714 | CA02 | 1 | harmonic U12 row 31 | 0.1% | 3 | 0XFFFF
| 51715 | CA03 | 1 | harmonic U23 row 31 | 0.1% | 3 | 0XFFFF
| 51716 | CA04 | 1 | harmonic U31 row 31 | 0.1% | 3 | 0XFFFF
| 51717 | CA05 | 1 | harmonic U12 row 33 | 0.1% | 3 | 0XFFFF
| 51718 | CA06 | 1 | harmonic U23 row 33 | 0.1% | 3 | 0XFFFF
| 51719 | CA07 | 1 | harmonic U31 row 33 | 0.1% | 3 | 0XFFFF
| 51720 | CA08 | 1 | harmonic U12 row 35 | 0.1% | 3 | 0XFFFF
| 51721 | CA09 | 1 | harmonic U23 row 35 | 0.1% | 3 | 0XFFFF
| 51722 | CA0A | 1 | harmonic U31 row 35 | 0.1% | 3 | 0XFFFF
| 51723 | CA0B | 1 | harmonic U12 row 37 | 0.1% | 3 | 0XFFFF
| 51724 | CA0C | 1 | harmonic U23 row 37 | 0.1% | 3 | 0XFFFF
| 51725 | CA0D | 1 | harmonic U31 row 37 | 0.1% | 3 | 0XFFFF
| 51726 | CA0E | 1 | harmonic U12 row 39 | 0.1% | 3 | 0XFFFF
| 51727 | CA0F | 1 | harmonic U23 row 39 | 0.1% | 3 | 0XFFFF
| 51728 | CA10 | 1 | harmonic U31 row 39 | 0.1% | 3 | 0XFFFF
| 51729 | CA11 | 1 | harmonic U12 row 41 | 0.1% | 3 | 0XFFFF
| 51730 | CA12 | 1 | harmonic U23 row 41 | 0.1% | 3 | 0XFFFF
| 51731 | CA13 | 1 | harmonic U31 row 41 | 0.1% | 3 | 0XFFFF
| 51732 | CA14 | 1 | harmonic U12 row 43 | 0.1% | 3 | 0XFFFF
| 51733 | CA15 | 1 | harmonic U23 row 43 | 0.1% | 3 | 0XFFFF
| 51734 | CA16 | 1 | harmonic U31 row 43 | 0.1% | 3 | 0XFFFF
| 51735 | CA17 | 1 | harmonic U12 row 45 | 0.1% | 3 | 0XFFFF
| 51736 | CA18 | 1 | harmonic U23 row 45 | 0.1% | 3 | 0XFFFF
| 51737 | CA19 | 1 | harmonic U31 row 45 | 0.1% | 3 | 0XFFFF
| 51738 | CA1A | 1 | harmonic U12 row 47 | 0.1% | 3 | 0XFFFF
| 51739 | CA1B | 1 | harmonic U23 row 47 | 0.1% | 3 | 0XFFFF
| 51740 | CA1C | 1 | harmonic U31 row 47 | 0.1% | 3 | 0XFFFF
| 51741 | CA1D | 1 | harmonic U12 row 49 | 0.1% | 3 | 0XFFFF
| 51742 | CA1E | 1 | harmonic U23 row 49 | 0.1% | 3 | 0XFFFF
| 51743 | CA1F | 1 | harmonic U31 row 49 | 0.1% | 3 | 0XFFFF
| 51744 | CA20 | 1 | harmonic U12 row 51 | 0.1% | 3 | 0XFFFF
| 51745 | CA21 | 1 | harmonic U23 row 51 | 0.1% | 3 | 0XFFFF
| 51746 | CA22 | 1 | harmonic U31 row 51 | 0.1% | 3 | 0XFFFF
| 51747 | CA23 | 1 | harmonic U12 row 53 | 0.1% | 3 | 0XFFFF
| 51748 | CA24 | 1 | harmonic U23 row 53 | 0.1% | 3 | 0XFFFF
| 51749 | CA25 | 1 | harmonic U31 row 53 | 0.1% | 3 | 0XFFFF
| 51750 | CA26 | 1 | harmonic U12 row 55 | 0.1% | 3 | 0XFFFF
| 51751 | CA27 | 1 | harmonic U23 row 55 | 0.1% | 3 | 0XFFFF
| 51752 | CA28 | 1 | harmonic U31 row 55 | 0.1% | 3 | 0XFFFF
| 51753 | CA29 | 1 | harmonic U12 row 57 | 0.1% | 3 | 0XFFFF
| 51754 | CA2A | 1 | harmonic U23 row 57 | 0.1% | 3 | 0XFFFF
| 51755 | CA2B | 1 | harmonic U31 row 57 | 0.1% | 3 | 0XFFFF
| 51756 | CA2C | 1 | harmonic U12 row 59 | 0.1% | 3 | 0XFFFF
| 51757 | CA2D | 1 | harmonic U23 row 59 | 0.1% | 3 | 0XFFFF
| 51758 | CA2E | 1 | harmonic U31 row 59 | 0.1% | 3 | 0XFFFF
| 51759 | CA2F | 1 | harmonic U12 row 61 | 0.1% | 3 | 0XFFFF
| 51760 | CA30 | 1 | harmonic U23 row 61 | 0.1% | 3 | 0XFFFF
| 51761 | CA31 | 1 | harmonic U31 row 61 | 0.1% | 3 | 0XFFFF
| 51762 | CA32 | 1 | harmonic U12 row 63 | 0.1% | 3 | 0XFFFF
| 51763 | CA33 | 1 | harmonic U23 row 63 | 0.1% | 3 | 0XFFFF
| 51764 | CA34 | 1 | harmonic U31 row 63 | 0.1% | 3 | 0XFFFF
| 51671 | C9D7 | 94
V PH/N : harmonic order
| 51765 | CA35 | 1 | Number of harmonic rows |  | 3 | 0
| 51766 | CA36 | 1 | harmonic V1 row 3 | 0.1% | 3 | 0xFFFF
| 51767 | CA37 | 1 | harmonic V2 row 3 | 0.1% | 3 | 0xFFFF
| 51768 | CA38 | 1 | harmonic V3 row 3 | 0.1% | 3 | 0xFFFF
| 51769 | CA39 | 1 | harmonic V1 row 5 | 0.1% | 3 | 0xFFFF
| 51770 | CA3A | 1 | harmonic V2 row 5 | 0.1% | 3 | 0xFFFF
| 51771 | CA3B | 1 | harmonic V3 row 5 | 0.1% | 3 | 0xFFFF
| 51772 | CA3C | 1 | harmonic V1 row 7 | 0.1% | 3 | 0xFFFF
| 51773 | CA3D | 1 | harmonic V2 row 7 | 0.1% | 3 | 0xFFFF
| 51774 | CA3E | 1 | harmonic V3 row 7 | 0.1% | 3 | 0xFFFF
| 51775 | CA3F | 1 | harmonic V1 row 9 | 0.1% | 3 | 0xFFFF
| 51776 | CA40 | 1 | harmonic V2 row 9 | 0.1% | 3 | 0xFFFF
| 51777 | CA41 | 1 | harmonic V3 row 9 | 0.1% | 3 | 0xFFFF
| 51778 | CA42 | 1 | harmonic V1 row 11 | 0.1% | 3 | 0xFFFF
| 51779 | CA43 | 1 | harmonic V2 row 11 | 0.1% | 3 | 0xFFFF
| 51780 | CA44 | 1 | harmonic V3 row 11 | 0.1% | 3 | 0xFFFF
| 51781 | CA45 | 1 | harmonic V1 row 13 | 0.1% | 3 | 0xFFFF
| 51782 | CA46 | 1 | harmonic V2 row 13 | 0.1% | 3 | 0xFFFF
| 51783 | CA47 | 1 | harmonic V3 row 13 | 0.1% | 3 | 0xFFFF
| 51784 | CA48 | 1 | harmonic V1 row 15 | 0.1% | 3 | 0xFFFF
| 51785 | CA49 | 1 | harmonic V2 row 15 | 0.1% | 3 | 0xFFFF
| 51786 | CA4A | 1 | harmonic V3 row 15 | 0.1% | 3 | 0xFFFF
| 51787 | CA4B | 1 | harmonic V1 row 17 | 0.1% | 3 | 0xFFFF
| 51788 | CA4C | 1 | harmonic V2 row 17 | 0.1% | 3 | 0xFFFF
| 51789 | CA4D | 1 | harmonic V3 row 17 | 0.1% | 3 | 0xFFFF
| 51790 | CA4E | 1 | harmonic V1 row 19 | 0.1% | 3 | 0xFFFF
| 51791 | CA4F | 1 | harmonic V2 row 19 | 0.1% | 3 | 0xFFFF
| 51792 | CA50 | 1 | harmonic V3 row 19 | 0.1% | 3 | 0xFFFF
| 51793 | CA51 | 1 | harmonic V1 row 21 | 0.1% | 3 | 0xFFFF
| 51794 | CA52 | 1 | harmonic V2 row 21 | 0.1% | 3 | 0xFFFF
| 51795 | CA53 | 1 | harmonic V3 row 21 | 0.1% | 3 | 0xFFFF
| 51796 | CA54 | 1 | harmonic V1 row 23 | 0.1% | 3 | 0xFFFF
| 51797 | CA55 | 1 | harmonic V2 row 23 | 0.1% | 3 | 0xFFFF
| 51798 | CA56 | 1 | harmonic V3 row 23 | 0.1% | 3 | 0xFFFF
| 51799 | CA57 | 1 | harmonic V1 row 25 | 0.1% | 3 | 0xFFFF
| 51800 | CA58 | 1 | harmonic V2 row 25 | 0.1% | 3 | 0xFFFF
| 51801 | CA59 | 1 | harmonic V3 row 25 | 0.1% | 3 | 0xFFFF
| 51802 | CA5A | 1 | harmonic V1 row 27 | 0.1% | 3 | 0xFFFF
| 51803 | CA5B | 1 | harmonic V2 row 27 | 0.1% | 3 | 0xFFFF
| 51804 | CA5C | 1 | harmonic V3 row 27 | 0.1% | 3 | 0xFFFF
| 51805 | CA5D | 1 | harmonic V1 row 29 | 0.1% | 3 | 0xFFFF
| 51806 | CA5E | 1 | harmonic V2 row 29 | 0.1% | 3 | 0xFFFF
| 51807 | CA5F | 1 | harmonic V3 row 29 | 0.1% | 3 | 0xFFFF
| 51808 | CA60 | 1 | harmonic V1 row 31 | 0.1% | 3 | 0xFFFF
| 51809 | CA61 | 1 | harmonic V2 row 31 | 0.1% | 3 | 0xFFFF
| 51810 | CA62 | 1 | harmonic V3 row 31 | 0.1% | 3 | 0xFFFF
| 51811 | CA63 | 1 | harmonic V1 row 33 | 0.1% | 3 | 0xFFFF
| 51812 | CA64 | 1 | harmonic V2 row 33 | 0.1% | 3 | 0xFFFF
| 51813 | CA65 | 1 | harmonic V3 row 33 | 0.1% | 3 | 0xFFFF
| 51814 | CA66 | 1 | harmonic V1 row 35 | 0.1% | 3 | 0xFFFF
| 51815 | CA67 | 1 | harmonic V2 row 35 | 0.1% | 3 | 0xFFFF
| 51816 | CA68 | 1 | harmonic V3 row 35 | 0.1% | 3 | 0xFFFF
| 51817 | CA69 | 1 | harmonic V1 row 37 | 0.1% | 3 | 0xFFFF
| 51818 | CA6A | 1 | harmonic V2 row 37 | 0.1% | 3 | 0xFFFF
| 51819 | CA6B | 1 | harmonic V3 row 37 | 0.1% | 3 | 0xFFFF
| 51820 | CA6C | 1 | harmonic V1 row 39 | 0.1% | 3 | 0xFFFF
| 51821 | CA6D | 1 | harmonic V2 row 39 | 0.1% | 3 | 0xFFFF
| 51822 | CA6E | 1 | harmonic V3 row 39 | 0.1% | 3 | 0xFFFF
| 51823 | CA6F | 1 | harmonic V1 row 41 | 0.1% | 3 | 0xFFFF
| 51824 | CA70 | 1 | harmonic V2 row 41 | 0.1% | 3 | 0xFFFF
| 51825 | CA71 | 1 | harmonic V3 row 41 | 0.1% | 3 | 0xFFFF
| 51826 | CA72 | 1 | harmonic V1 row 43 | 0.1% | 3 | 0xFFFF
| 51827 | CA73 | 1 | harmonic V2 row 43 | 0.1% | 3 | 0xFFFF
| 51828 | CA74 | 1 | harmonic V3 row 43 | 0.1% | 3 | 0xFFFF
| 51829 | CA75 | 1 | harmonic V1 row 45 | 0.1% | 3 | 0xFFFF
| 51830 | CA76 | 1 | harmonic V2 row 45 | 0.1% | 3 | 0xFFFF
| 51831 | CA77 | 1 | harmonic V3 row 45 | 0.1% | 3 | 0xFFFF
| 51832 | CA78 | 1 | harmonic V1 row 47 | 0.1% | 3 | 0xFFFF
| 51833 | CA79 | 1 | harmonic V2 row 47 | 0.1% | 3 | 0xFFFF
| 51834 | CA7A | 1 | harmonic V3 row 47 | 0.1% | 3 | 0xFFFF
| 51835 | CA7B | 1 | harmonic V1 row 49 | 0.1% | 3 | 0xFFFF
| 51836 | CA7C | 1 | harmonic V2 row 49 | 0.1% | 3 | 0xFFFF
| 51837 | CA7D | 1 | harmonic V3 row 49 | 0.1% | 3 | 0xFFFF
| 51838 | CA7E | 1 | harmonic V1 row 51 | 0.1% | 3 | 0xFFFF
| 51839 | CA7F | 1 | harmonic V2 row 51 | 0.1% | 3 | 0xFFFF
| 51840 | CA80 | 1 | harmonic V3 row 51 | 0.1% | 3 | 0xFFFF
| 51841 | CA81 | 1 | harmonic V1 row 53 | 0.1% | 3 | 0xFFFF
| 51842 | CA82 | 1 | harmonic V2 row 53 | 0.1% | 3 | 0xFFFF
| 51843 | CA83 | 1 | harmonic V3 row 53 | 0.1% | 3 | 0xFFFF
| 51844 | CA84 | 1 | harmonic V1 row 55 | 0.1% | 3 | 0xFFFF
| 51845 | CA85 | 1 | harmonic V2 row 55 | 0.1% | 3 | 0xFFFF
| 51846 | CA86 | 1 | harmonic V3 row 55 | 0.1% | 3 | 0xFFFF
| 51847 | CA87 | 1 | harmonic V1 row 57 | 0.1% | 3 | 0xFFFF
| 51848 | CA88 | 1 | harmonic V2 row 57 | 0.1% | 3 | 0xFFFF
| 51849 | CA89 | 1 | harmonic V3 row 57 | 0.1% | 3 | 0xFFFF
| 51850 | CA8A | 1 | harmonic V1 row 59 | 0.1% | 3 | 0xFFFF
| 51851 | CA8B | 1 | harmonic V2 row 59 | 0.1% | 3 | 0xFFFF
| 51852 | CA8C | 1 | harmonic V3 row 59 | 0.1% | 3 | 0xFFFF
| 51853 | CA8D | 1 | harmonic V1 row 61 | 0.1% | 3 | 0xFFFF
| 51854 | CA8E | 1 | harmonic V2 row 61 | 0.1% | 3 | 0xFFFF
| 51855 | CA8F | 1 | harmonic V3 row 61 | 0.1% | 3 | 0xFFFF
| 51856 | CA90 | 1 | harmonic V1 row 63 | 0.1% | 3 | 0xFFFF
| 51857 | CA91 | 1 | harmonic V2 row 63 | 0.1% | 3 | 0xFFFF
| 51858 | CA92 | 1 | harmonic V3 row 63 | 0.1% | 3 | 0xFFFF
| 51765 | CA35 | 94
| 51536 | C950 | 323
CB00 Hex : Input/Output state
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function | Value if not Available
| 51968 | CB00 | 1 | Input count |  | 3 | 0
| 51969 | CB01 | 1 | Bit 0 : Input 1 Open or Closed Bit x : Input x Open or Closed | Bitfield | 3
| 51970 | CB02 | 1 | Output count |  | 3 | 0
| 51971 | CB03 | 1 | Bit 0 : Output 1 Open or Closed Bit x : Output x Open or Closed | Bitfield | 3
| 51968 | CB00 | 4
E000 Hex : Network Setting
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function | Value if not Available
| 57344 | E000 | 1 | Network Type : 0 : 1BL 1 : 2BL 2 : 3BL 3 : 3NBL 4 : 4BL 5 : 4NBL 6 : 2NBL | – | 3,6,16 | 0xFFFF
| 57345 | E001 | 1 | Current Transformer secondary : 1: 1 A 5: 5 A | A | 3,6,16 | 0xFFFF
| 57346 | E002 | 1 | Current Transformer primary | A | 3,6,16 | 0xFFFF
| 57347 | E003 | 1 | Neutral Current Transformer present : 0 : No 1: Yes | – | 3,6,16 | 0xFFFF
| 57348 | E004 | 1 | Neutral Current Transformer secondary: 1: 1 A 5: 5 A | A | 3,6,16 | 0xFFFF
| 57349 | E005 | 1 | Neutral Current Transformer primary | A | 3,6,16 | 0xFFFF
| 57350 | E006 | 1 | Voltage transformer present : 0 : No 1: Yes | – | 3,6,16 | 0xFFFF
| 57351 | E007 | 1 | Voltage Transformersecondary : 60 : 60 V 100 : 100 V 110 : 110 V 115 : 115 V 120 : 120 V 173 : 173 V 190 : 190 V | V | 3,6,16 | 0xFFFF
| 57352 | E008 | 2 | Voltage Transformer primary | V | 3,6,16 | 0xFFFFFFFF
| 57354 | E00A | 1 | Internal/External Top | 0:internal / 1:external | 3,6,16 | 0xFFFF
| 57355 | E00B | 1 | Synchronisation Top for P+/- Q+/- : time in seconds ( 2mn, 5mn, 8mn, 10mn, 15mn, 20mn, 30mn, 60mn) | secondes | 3,6,16 | 0xFFFF
| 57344 | E000 | 12
E100 Hex :Hour/Date setting ( Write 6 words in one time Function 16)
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 57600 | E100 | 1 | Day |  | 3.16
| 57601 | E101 | 1 | Month |  | 3.16
| 57602 | E102 | 1 | Year |  | 3.16
| 57603 | E103 | 1 | Hour |  | 3.16
| 57604 | E104 | 1 | Minute |  | 3.16
| 57605 | E105 | 1 | Second |  | 3.16
| 57600 | E100 | 6
E110 Hex : Ethernet module JBUS interface
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 57616 | E110 | 1 | IP = Part 1 . Part 2 . Part3 . Part4 Ethernet IP address - part 1 | 0 - 255 | 3,6,16
| 57617 | E111 | 1 | Ethernet IP address - part 2 | 0 - 255 | 3,6,16
| 57618 | E112 | 1 | Ethernet IP address - part 3 | 0 - 255 | 3,6,16
| 57619 | E113 | 1 | Ethernet IP address - part 4 | 0 - 255 | 3,6,16
| 57620 | E114 | 1 | Ethernet GATE - part 1 | 0 - 255 | 3,6,16
| 57621 | E115 | 1 | Ethernet GATE - part 2 | 0 - 255 | 3,6,16
| 57622 | E116 | 1 | Ethernet GATE - part 3 | 0 - 255 | 3,6,16
| 57623 | E117 | 1 | Ethernet GATE - part 4 | 0 - 255 | 3,6,16
| 57624 | E118 | 1 | Ethernet MASK - part 1 | 0 - 255 | 3,6,16
| 57625 | E119 | 1 | Ethernet MASK - part 2 | 0 - 255 | 3,6,16
| 57626 | E11A | 1 | Ethernet MASK - part 3 | 0 - 255 | 3,6,16
| 57627 | E11B | 1 | Ethernet MASK - part 4 | 0 - 255 | 3,6,16
| 57628 | E11C | 1 | DHCP used | yes(1) / no (0) | 3,6,16
| 57629 | E11D | 1 | JBUS gateway enabled | yes(1) / no (0) | 3,6,16
| 57630 | E11E | 1 | JBUS RTU over Ethernet Enabled | yes(1) / no (0) | 3,6,16
| 57631 | E11F | 1 | Gateway External JBUS Baudrate enumeration | 0 = 2400 bps 1 = 4800 bps 2 = 9600 bps 3 = 19200 bps 4 = 38400 bps | 3,6,16
| 57632 | E120 | 1 | Gateway External JBUS Parity | 0 = none 1 = even 2 = odd | 3,6,16
| 57633 | E121 | 1 | Gateway External JBUS Stopbit | 0 = 1 stop bit 1 = 2 stop bits | 3,6,16
| 57634 | E122 | 1 | JBUS Gateway Master request timeout | ms | 3,6,16
| 57635 | E123 | 1 | JBUS Slave address (RS485 & RTU over Ethernet) | 1-247 | 3,6,16
| 57616 | E110 | 20
E200 Hex : Action system ( Write Function only )
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| 57856 | E200 | 1 | Action : 0xA1 : Product Configuration storage 0xB2 : Produit reboot |  | 6
| 57856 | E200 | 1
SM103E specific tables
300 Hex : Measurement CT/VT affected
| Address Dec. | Address Hex. | Word Count | Description | Unit | Function
| 768 | 300 | 2 | Phase 1 Current | mA | 3
| 770 | 302 | 2 | Phase 2 Current | mA | 3
| 772 | 304 | 2 | Phase 3 Current | mA | 3
| 774 | 306 | 2 | Neutral Current | mA | 3
| 776 | 308 | 2 | Phase to Phase Voltage: U12 | V/100 | 3
| 778 | 30A | 2 | Phase to Phase Voltage: U23 | V/100 | 3
| 780 | 30C | 2 | Phase to Phase Voltage: U31 | V/100 | 3
| 782 | 30E | 2 | Phase to Neutral voltage phase 1 | V/100 | 3
| 784 | 310 | 2 | Phase to Neutral voltage phase 2 | V/100 | 3
| 786 | 312 | 2 | Phase to Neutral voltage phase 3 | V/100 | 3
| 788 | 314 | 2 | Frequency | Hz/100 | 3
| 790 | 316 | 2 | ∑ active power +/- : P | kW/100 | 3
| 792 | 318 | 2 | ∑ reactive power +/- : Q | kvar/100 | 3
| 794 | 31A | 2 | ∑ apparent power : S | kVA/100 | 3
| 796 | 31C | 2 | ∑ power factor : -: leadiing et + : lagging : PF | 0.001 | 3
| 798 | 31E | 2 | Active Power phase1 +/- | kW/100 | 3
| 800 | 320 | 2 | Active Power phase2 +/- | kW/100 | 3
| 802 | 322 | 2 | Active Power phase3 +/- | kW/100 | 3
| 804 | 324 | 2 | Reactive Power phase1 +/- | kVar/100 | 3
| 806 | 326 | 2 | Reactive Power phase2 +/- | kVar/100 | 3
| 808 | 328 | 2 | Reactive Power phase3 +/- | kVar/100 | 3
| 810 | 32A | 2 | Apparent Power phase1 | kVa/100 | 3
| 812 | 32C | 2 | Apparent Power phase2 | kVa/100 | 3
| 814 | 32E | 2 | Apparent Power phase3 | kVa/100 | 3
| 816 | 330 | 2 | Power factor phase 1 -:leading and +: lagging | 0.001 | 3
| 818 | 332 | 2 | Power factor phase 2 -:leading and +: lagging | 0.001 | 3
| 820 | 334 | 2 | Power factor phase 3 -:leading and +: lagging | 0.001 | 3
| 822 | 336 | 2 | avg I1 | mA | 3
| 824 | 338 | 2 | avg I2 | mA | 3
| 826 | 33A | 2 | avg I3 | mA | 3
| 828 | 33C | 2 | avg ∑active power + | kW/100 | 3
| 830 | 33E | 2 | avg ∑active power - | kW/100 | 3
| 832 | 340 | 2 | avg ∑reactive power + | kVar/100 | 3
| 834 | 342 | 2 | avg ∑reactive power - | kVar/100 | 3
| 836 | 344 | 2 | avg ∑ apparent power | kVa/100 | 3
| 838 | 346 | 2 | max/avg I1 | mA | 3
| 840 | 348 | 2 | max/avg I2 | mA | 3
| 842 | 34A | 2 | max/avg I3 | mA | 3
| 844 | 34C | 2 | max/avg ∑active power + | kW/100 | 3
| 846 | 34E | 2 | max/avg ∑active power - | kW/100 | 3
| 848 | 350 | 2 | max/avg ∑reactive power + | kVar/100 | 3
| 850 | 352 | 2 | max/avg ∑reactive power - | kVar/100 | 3
| 852 | 354 | 2 | max/avg ∑ apparent power | kVa/100 | 3
| 854 | 356 | 2 | Hour meter | Hour/100 | 3
| 856 | 358 | 2 | Active Energy + | kWh | 3
| 858 | 35A | 2 | Reactive Energy + | kvarh | 3
| 860 | 35C | 2 | Apparent Energy | kVAh | 3
| 862 | 35E | 2 | Active Energy - | kWh | 3
| 864 | 360 | 2 | Reactive Energy - | kvarh | 3
| 866 | 362 | 2 | Input pulse meter 1 | - | 3
| 868 | 364 | 2 | Input pulse meter 2 | - | 3
| 870 | 366 | 2 | Number of input pulse meters | - | 3
| 872 | 368 | 2 | Alarm in progress (Timer finished) - bit field: bit 1: I bit 2: In bit 3: U bit 4: V bit 5: ∑P+ bit 6: ∑Q+ bit 7: ∑S bit 8: F bit 9: ∑PF (L) bit 10: Time bit 11: THD I bit 12: THD In bit 13: THD U bit 14: THD V bit 15: ∑P- bit 16: ∑Q- bit 17: ∑PF (C) bit 18: T°C 1 bit 19: T°C 2 bit 20: T°C 3 bit 21: T°C 4 bit 22: P Predicted bit 23: Q predicted bit 24: S Predicted | - | 3
| 874 | 36A | 2 | Alarm detected (Timer in progress) - bit field: bit 1: I bit 2: In bit 3: U bit 4: V bit 5: ∑P+ bit 6: ∑Q+ bit 7: ∑S bit 8: F bit 9: ∑PF (L) bit 10: Time bit 11: THD I bit 12: THD In bit 13: THD U bit 14: THD V bit 15: ∑P- bit 16: ∑Q- bit 17: ∑PF (C) bit 18: T°C 1 bit 19: T°C 2 bit 20: T°C 3 bit 21: T°C 4 bit 22: P Predicted bit 23: Q predicted bit 24: S Predicted | - | R
| 876 | 36C | 2 | Number of inputs-outputs : Low_order: number of inputs : High-order: number of outputs | - | 3
| 878 | 36E | 2 | Status of inputs-outputs bit 0 : status input 1 (0 = open, 1 = closed) bit 1 : status input 2 (0 = open, 1 = closed) bit 2 : status input 3 (0 = open, 1 = closed) bit 3 : status input 4 (0 = open, 1 = closed) bit 4 : status input 5 (0 = open, 1 = closed) bit 5 : status input 6 (0 = open, 1 = closed) bit 16 : statuis output 1 (0 = open, 1 = closed) bit 17 : statuis output 2 (0 = open, 1 = closed) bit 18 : statuis output 3 (0 = open, 1 = closed) bit 19 : statuis output 4 (0 = open, 1 = closed) bit 20 : statuis output 5 (0 = open, 1 = closed) bit 21 : statuis output 6 (0 = open, 1 = closed) | - | 3
| 880 | 370 | 2 | System value for current | mA | 3
| 882 | 372 | 2 | System value for phase to phase voltage | V/100 | 3
| 884 | 374 | 2 | System value for phase to neutral voltage | V/100 | 3
| 886 | 376 | 2 | avg U12 | V/100 | 3
| 888 | 378 | 2 | avg U23 | V/100 | 3
| 890 | 37A | 2 | avg U31 | V/100 | 3
| 892 | 37C | 2 | avg V1 | V/100 | 3
| 894 | 37E | 2 | avg V2 | V/100 | 3
| 896 | 380 | 2 | avg V3 | V/100 | 3
| 898 | 382 | 2 | avg F | HZ/100 | 3
| 900 | 384 | 2 | max/avg U12 | V/100 | 3
| 902 | 386 | 2 | max/avg U23 | V/100 | 3
| 904 | 388 | 2 | max/avg U31 | V/100 | 3
| 906 | 38A | 2 | max/avg V1 | V/100 | 3
| 908 | 38C | 2 | max/avg V2 | V/100 | 3
| 910 | 38E | 2 | max/avg V3 | V/100 | 3
| 912 | 390 | 2 | max/avg F | HZ/100 | 3
| 914 | 392 | 2 | avg In | mA | 3
| 916 | 394 | 2 | max/avg In | mA | 3
| 918 | 396 | 2 | Mean positive active power between 2 signals | 0,01 kWh | 3
| 920 | 398 | 2 | Mean negative active power between 2 signals | 0,01 kWh | 3
| 922 | 39A | 2 | Mean positive reactive power between 2 signals | 0,01 kVARh | 3
| 924 | 39C | 2 | Mean negative reactive power between 2 signals | 0,01 kVARh | 3
| 926 | 39E | 2 | Predictive total Reactive power | kW/100 | 3
| 928 | 3A0 | 2 | Predictive total Reactive power | kvar/100 | 3
| 930 | 3A2 | 2 | Predictive total Apparent power | kVA/100 | 3
| 768 | 300 | 164
700 Hex : Measurement NO CT/VT affected
| Address Dec. | Address Hex. | Word Count | Description | Unit | Function
| 1792 | 700 | 1 | Phase 1 Current | mA | 3
| 1793 | 701 | 1 | Phase 2 Current | mA | 3
| 1794 | 702 | 1 | Phase 3 Current | mA | 3
| 1795 | 703 | 1 | Neutral Current | mA | 3
| 1796 | 704 | 1 | Phase to Phase Voltage: U12 | V/100 | 3
| 1797 | 705 | 1 | Phase to Phase Voltage: U23 | V/100 | 3
| 1798 | 706 | 1 | Phase to Phase Voltage: U31 | V/100 | 3
| 1799 | 707 | 1 | Phase to Neutral voltage phase 1 | V/100 | 3
| 1800 | 708 | 1 | Phase to Neutral voltage phase 2 | V/100 | 3
| 1801 | 709 | 1 | Phase to Neutral voltage phase 3 | V/100 | 3
| 1802 | 70A | 1 | Frequency | Hz/100 | 3
| 1803 | 70B | 1 | ∑ active power +/- : P | kW/100 | 3
| 1804 | 70C | 1 | ∑ reactive power +/- : Q | kvar/100 | 3
| 1805 | 70D | 1 | ∑ apparent power : S | kVA/100 | 3
| 1806 | 70E | 1 | ∑ power factor : -: leadiing et + : lagging : PF | 0.001 | 3
| 1807 | 70F | 1 | Active Power phase1 +/- | kW/100 | 3
| 1808 | 710 | 1 | Active Power phase2 +/- | kW/100 | 3
| 1809 | 711 | 1 | Active Power phase3 +/- | kW/100 | 3
| 1810 | 712 | 1 | Reactive Power phase1 +/- | kVar/100 | 3
| 1811 | 713 | 1 | Reactive Power phase2 +/- | kVar/100 | 3
| 1812 | 714 | 1 | Reactive Power phase3 +/- | kVar/100 | 3
| 1813 | 715 | 1 | Apparent Power phase1 | kVa/100 | 3
| 1814 | 716 | 1 | Apparent Power phase2 | kVa/100 | 3
| 1815 | 717 | 1 | Apparent Power phase3 | kVa/100 | 3
| 1816 | 718 | 1 | Power factor phase 1 -:leading and +: lagging | 0.001 | 3
| 1817 | 719 | 1 | Power factor phase 2 -:leading and +: lagging | 0.001 | 3
| 1818 | 71A | 1 | Power factor phase 3 -:leading and +: lagging | 0.001 | 3
| 1819 | 71B | 1 | avg I1 | mA | 3
| 1820 | 71C | 1 | avg I2 | mA | 3
| 1821 | 71D | 1 | avg I3 | mA | 3
| 1822 | 71E | 1 | avg ∑active power + | kW/100 | 3
| 1823 | 71F | 1 | avg ∑active power - | kW/100 | 3
| 1824 | 720 | 1 | avg ∑reactive power + | kvar/100 | 3
| 1825 | 721 | 1 | avg ∑reactive power - | kvar/100 | 3
| 1826 | 722 | 1 | avg ∑ apparent power | kVA/100 | 3
| 1827 | 723 | 1 | max/avg I1 | mA | 3
| 1828 | 724 | 1 | max/avg I2 | mA | 3
| 1829 | 725 | 1 | max/avg I3 | mA | 3
| 1830 | 726 | 1 | max/avg ∑active power + | kW/100 | 3
| 1831 | 727 | 1 | max/avg ∑active power - |  | 3
| 1832 | 728 | 1 | max/avg ∑reactive power + | kVar/100 | 3
| 1833 | 729 | 1 | max/avg ∑reactive power - |  | 3
| 1834 | 72A | 1 | max/avg ∑ apparent power | kVa/100 | 3
| 1835 | 72B | 1 | Active Energy +<10 000 | kWh | 3
| 1836 | 72C | 1 | Active Energy +>10 000 | kWh | 3
| 1837 | 72D | 1 | Reactive Energy+< 10 000 | kvarh | 3
| 1838 | 72E | 1 | Reactive Energy +>10 000 | kvarh | 3
| 1839 | 72F | 1 | apparent Energy + < 10000 | kVAh | 3
| 1840 | 730 | 1 | apparent Energy + > 10000 | kVAh | 3
| 1841 | 731 | 1 | Active Energy- < 10000 | kWh | 3
| 1842 | 732 | 1 | Active Energy - >10000 | kWh | 3
| 1843 | 733 | 1 | Reactive Energy- < 10000 | kvarh | 3
| 1844 | 734 | 1 | Reactive Energy - > 10000 | kvarh | 3
| 1845 | 735 | 1 | input pulse meter 1 < 10000 | – | 3
| 1846 | 736 | 1 | input pulse meter 1 > 10000 | – | 3
| 1847 | 737 | 1 | input pulse meter 2 < 10000 | – | 3
| 1848 | 738 | 1 | input pulse meter 2 > 10000 | – | 3
| 1849 | 739 | 1 | input pulse meter 3 < 10000 | – | 3
| 1850 | 73A | 1 | input pulse meter 3 > 10000 | – | 3
| 1851 | 73B | 1 | input pulse meter 4 < 10000 | – | 3
| 1852 | 73C | 1 | input pulse meter 4 > 10000 | – | 3
| 1853 | 73D | 1 | input pulse meter 5 < 10000 | – | 3
| 1854 | 73E | 1 | input pulse meter 5 > 10000 | – | 3
| 1855 | 73F | 1 | input pulse meter 6 < 10000 | – | 3
| 1856 | 740 | 1 | input pulse meter 6 > 10000 | – | 3
| 1857 | 741 | 1 | System value I Sys = ( I1+I2+I3) / 3 | mA | 3
| 1858 | 742 | 1 | System value U Sys = (U12 + U23 + U31 ) / 3 | V/100 | 3
| 1859 | 743 | 1 | System value V Sys = (V1 + V2 + V3 ) / 3 | V/100 | 3
| 1860 | 744 | 1 | Minimum of Current on 3 phases | mA | 3
| 1861 | 745 | 1 | Minimum of In | mA | 3
| 1862 | 746 | 1 | Minimum of phase to phase voltage on 3 phases | V/100 | 3
| 1863 | 747 | 1 | Minimum of Frequency | Hz/100 | 3
| 1864 | 748 | 1 | Maximum of Current on 3 phases | mA | 3
| 1865 | 749 | 1 | Maximum of AVG In | mA | 3
| 1866 | 74A | 1 | Maximum of phase to phase voltage on 3 phases | V/100 | 3
| 1867 | 74B | 1 | Maximum of AVG Frequency | Hz/100 | 3
| 1868 | 74C | 1 | Minimum of power factor | 0.001 | 3
| 1869 | 74D | 1 | Minimum of Active power +/- | kW/100 | 3
| 1870 | 74E | 1 | Minimum of Reactive power +/- | kvar/100 | 3
| 1871 | 74F | 1 | Maximum of factor | 0.001 | 3
| 1872 | 750 | 1 | Maximum of Active power +/- | kW/100 | 3
| 1873 | 751 | 1 | Maximum of Reactive power +/- | kvar/100 | 3
| 1874 | 752 | 1 | thd I1 | 0.1% | 3
| 1875 | 753 | 1 | thd I2 | 0.1% | 3
| 1876 | 754 | 1 | thd I3 | 0.1% | 3
| 1877 | 755 | 1 | thd In | 0.1% | 3
| 1878 | 756 | 1 | thd U12 | 0.1% | 3
| 1879 | 757 | 1 | thd U23 | 0.1% | 3
| 1880 | 758 | 1 | thd U31 | 0.1% | 3
| 1881 | 759 | 1 | thd V1 | 0.1% | 3
| 1882 | 75A | 1 | thd V2 | 0.1% | 3
| 1883 | 75B | 1 | thd V3 | 0.1% | 3
| 1884 | 75C | 1 | Mean positive active power between 2 signals | 0,1 W | 3
| 1885 | 75D | 1 | Mean negative active power between 2 signals | 0,1 W | 3
| 1886 | 75E | 1 | Mean positive reactive power between 2 signals | 0,1 var | 3
| 1887 | 75F | 1 | Mean negative reactive power between 2 signals | 0,1 var | 3
| 1888 | 760 | 1 | Reserved | - | 3
| 1889 | 761 | 1 | Reserved | - | 3
| 1890 | 762 | 1 | AVG In | mA | 3
| 1891 | 763 | 1 | Max / AVG In | mA | 3
| 1892 | 764 | 1 | Predictive total Active power | W | 3
| 1893 | 765 | 1 | Predictive total Reactive power | Vars | 3
| 1894 | 766 | 1 | Predictive total Apparent power | VA | 3
| 1792 | 700 | 103
900 Hex : THD
| Address Dec. | Address Hex. | Word Count | Description | Unit | Function
| 2304 | 900 | 1 | thd I1 | 0.1% | 3
| 2305 | 901 | 1 | thd I2 | 0.1% | 3
| 2306 | 902 | 1 | thd I3 | 0.1% | 3
| 2307 | 903 | 1 | thd In | 100.1% | 3
| 2308 | 904 | 1 | thd U12 | 0.1% | 3
| 2309 | 905 | 1 | thd U23 | 0.1% | 3
| 2310 | 906 | 1 | thd U31 | 0.1% | 3
| 2311 | 907 | 1 | thd V1 | 0.1% | 3
| 2312 | 908 | 1 | thd V2 | 0.1% | 3
| 2313 | 909 | 1 | thd V3 | 0.1% | 3
| 2314 | 90A | 1 | Harmonic I1 row 3 | 0.1% | 3
| 2315 | 90B | 1 | harmonic I2 row 3 | 0.1% | 3
| 2316 | 90C | 1 | Harmonic I3 row 3 | 0.1% | 3
| 2317 | 90D | 1 | Harmonic IN row 3 | 0.1% | 3
| 2318 | 90E | 1 | Harmonic I1 row 5 | 0.1% | 3
| 2319 | 90F | 1 | Harmonic I2 row 5 | 0.1% | 3
| 2320 | 910 | 1 | Harmonic I3 row 5 | 0.1% | 3
| 2321 | 911 | 1 | Harmonic IN row 5 | 0.1% | 3
| 2322 | 912 | 1 | Harmonic I1 row 7 | 0.1% | 3
| 2323 | 913 | 1 | Harmonic I2 row 7 | 0.1% | 3
| 2324 | 914 | 1 | Harmonic I3 row 7 | 0.1% | 3
| 2325 | 915 | 1 | Harmonic IN row 7 | 0.1% | 3
| 2326 | 916 | 1 | Harmonic I1 row 9 | 0.1% | 3
| 2327 | 917 | 1 | Harmonic I2 row 9 | 0.1% | 3
| 2328 | 918 | 1 | Harmonic I3 row 9 | 0.1% | 3
| 2329 | 919 | 1 | Harmonic IN row 9 | 0.1% | 3
| 2330 | 91A | 1 | Harmonic I1 row 11 | 0.1% | 3
| 2331 | 91B | 1 | Harmonic I2 row 11 | 0.1% | 3
| 2332 | 91C | 1 | Harmonic I3 row 11 | 0.1% | 3
| 2333 | 91D | 1 | Harmonic IN row 11 | 0.1% | 3
| 2334 | 91E | 1 | Harmonic I1 row 13 | 0.1% | 3
| 2335 | 91F | 1 | Harmonic I2 row 13 | 0.1% | 3
| 2336 | 920 | 1 | Harmonic I3 row 13 | 0.1% | 3
| 2337 | 921 | 1 | Harmonic IN row 13 | 0.1% | 3
| 2338 | 922 | 1 | Harmonic I1 row 15 | 0.1% | 3
| 2339 | 923 | 1 | Harmonic I2 row 15 | 0.1% | 3
| 2340 | 924 | 1 | Harmonic I3 row 15 | 0.1% | 3
| 2341 | 925 | 1 | Harmonic IN row 15 | 0.1% | 3
| 2342 | 926 | 1 | Harmonic U12 row 3 | 0.1% | 3
| 2343 | 927 | 1 | Harmonic U23 row 3 | 0.1% | 3
| 2344 | 928 | 1 | Harmonic U31 row 3 | 0.1% | 3
| 2345 | 929 | 1 | Harmonic U12 row 5 | 0.1% | 3
| 2346 | 92A | 1 | Harmonic U23 row 5 | 0.1% | 3
| 2347 | 92B | 1 | Harmonic U31 row 5 | 0.1% | 3
| 2348 | 92C | 1 | Harmonic U12 row 7 | 0.1% | 3
| 2349 | 92D | 1 | Harmonic U23 row 7 | 0.1% | 3
| 2350 | 92E | 1 | Harmonic U31 row 7 | 0.1% | 3
| 2351 | 92F | 1 | Harmonic U12 row 9 | 0.1% | 3
| 2352 | 930 | 1 | Harmonic U23 row 9 | 0.1% | 3
| 2353 | 931 | 1 | Harmonic U31 row 9 | 0.1% | 3
| 2354 | 932 | 1 | Harmonic U12 row 11 | 0.1% | 3
| 2355 | 933 | 1 | Harmonic U23 row 11 | 0.1% | 3
| 2356 | 934 | 1 | Harmonic U31 row 11 | 0.1% | 3
| 2357 | 935 | 1 | Harmonic U12 row 13 | 0.1% | 3
| 2358 | 936 | 1 | Harmonic U23 row 13 | 0.1% | 3
| 2359 | 937 | 1 | Harmonic U31 row 13 | 0.1% | 3
| 2360 | 938 | 1 | Harmonic U12 row 15 | 0.1% | 3
| 2361 | 939 | 1 | Harmonic U23 row 15 | 0.1% | 3
| 2362 | 93A | 1 | Harmonic U31 row 15 | 0.1% | 3
| 2363 | 93B | 1 | Harmonic V1 row 3 | 0.1% | 3
| 2364 | 93C | 1 | Harmonic V2 row 3 | 0.1% | 3
| 2365 | 93D | 1 | Harmonic V3 row 3 | 0.1% | 3
| 2366 | 93E | 1 | Harmonic V1 row 5 | 0.1% | 3
| 2367 | 93F | 1 | Harmonic V2 row 5 | 0.1% | 3
| 2368 | 940 | 1 | Harmonic V3 row 5 | 0.1% | 3
| 2369 | 941 | 1 | Harmonic V1 row 7 | 0.1% | 3
| 2370 | 942 | 1 | Harmonic V2 row 7 | 0.1% | 3
| 2371 | 943 | 1 | Harmonic V3 row 7 | 0.1% | 3
| 2372 | 944 | 1 | Harmonic V1 row 9 | 0.1% | 3
| 2373 | 945 | 1 | Harmonic V2 row 9 | 0.1% | 3
| 2374 | 946 | 1 | Harmonic V3 row 9 | 0.1% | 3
| 2375 | 947 | 1 | Harmonic V1 row 11 | 0.1% | 3
| 2376 | 948 | 1 | Harmonic V2 row 11 | 0.1% | 3
| 2377 | 949 | 1 | Harmonic V3 row 11 | 0.1% | 3
| 2378 | 94A | 1 | Harmonic V1 row 13 | 0.1% | 3
| 2379 | 94B | 1 | Harmonic V2 row 13 | 0.1% | 3
| 2380 | 94C | 1 | Harmonic V3 row 13 | 0.1% | 3
| 2381 | 94D | 1 | Harmonic V1 row 15 | 0.1% | 3
| 2382 | 94E | 1 | Harmonic V2 row 15 | 0.1% | 3
| 2383 | 94F | 1 | Harmonic V3 row 15 | 0.1% | 3
| 2384 | 950 | 1 | Harmonic I1 row 17 | 0.1% | 3
| 2385 | 951 | 1 | Harmonic I2 row 17 | 0.1% | 3
| 2386 | 952 | 1 | Harmonic I3 row 17 | 0.1% | 3
| 2387 | 953 | 1 | Harmonic IN row 17 | 0.1% | 3
| 2388 | 954 | 1 | Harmonic I1 row 19 | 0.1% | 3
| 2389 | 955 | 1 | Harmonic I2 row 19 | 0.1% | 3
| 2390 | 956 | 1 | Harmonic I3 row 19 | 0.1% | 3
| 2391 | 957 | 1 | Harmonic IN row 19 | 0.1% | 3
| 2392 | 958 | 1 | Harmonic I1 row 21 | 0.1% | 3
| 2393 | 959 | 1 | Harmonic I2 row 21 | 0.1% | 3
| 2394 | 95A | 1 | Harmonic I3 row 21 | 0.1% | 3
| 2395 | 95B | 1 | Harmonic IN row 21 | 0.1% | 3
| 2396 | 95C | 1 | Harmonic I1 row 23 | 0.1% | 3
| 2397 | 95D | 1 | Harmonic I2 row 23 | 0.1% | 3
| 2398 | 95E | 1 | Harmonic I3 row 23 | 0.1% | 3
| 2399 | 95F | 1 | Harmonic IN row 23 | 0.1% | 3
| 2400 | 960 | 1 | Harmonic I1 row 25 | 0.1% | 3
| 2401 | 961 | 1 | Harmonic I2 row 25 | 0.1% | 3
| 2402 | 962 | 1 | Harmonic I3 row 25 | 0.1% | 3
| 2403 | 963 | 1 | Harmonic IN row 25 | 0.1% | 3
| 2404 | 964 | 1 | Harmonic U12 row 17 | 0.1% | 3
| 2405 | 965 | 1 | Harmonic U23 row 17 | 0.1% | 3
| 2406 | 966 | 1 | Harmonic U31 row 17 | 0.1% | 3
| 2407 | 967 | 1 | Harmonic U12 row 19 | 0.1% | 3
| 2408 | 968 | 1 | Harmonic U23 row 19 | 0.1% | 3
| 2409 | 969 | 1 | Harmonic U31 row 19 | 0.1% | 3
| 2410 | 96A | 1 | Harmonic U12 row 21 | 0.1% | 3
| 2411 | 96B | 1 | Harmonic U23 row 21 | 0.1% | 3
| 2412 | 96C | 1 | Harmonic U31 row 21 | 0.1% | 3
| 2413 | 96D | 1 | Harmonic U12 row 23 | 0.1% | 3
| 2414 | 96E | 1 | Harmonic U23 row 23 | 0.1% | 3
| 2415 | 96F | 1 | Harmonic U31 row 23 | 0.1% | 3
| 2416 | 970 | 1 | Harmonic U12 row 25 | 0.1% | 3
| 2417 | 971 | 1 | Harmonic U23 row 25 | 0.1% | 3
| 2418 | 972 | 1 | Harmonic U31 row 25 | 0.1% | 3
| 2419 | 973 | 1 | Harmonic V1 row 17 | 0.1% | 3
| 2420 | 974 | 1 | Harmonic V2 row 17 | 0.1% | 3
| 2421 | 975 | 1 | Harmonic V3 row 17 | 0.1% | 3
| 2422 | 976 | 1 | Harmonic V1 row 19 | 0.1% | 3
| 2423 | 977 | 1 | Harmonic V2 row 19 | 0.1% | 3
| 2424 | 978 | 1 | Harmonic V3 row 19 | 0.1% | 3
| 2425 | 979 | 1 | Harmonic V1 row 21 | 0.1% | 3
| 2426 | 97A | 1 | Harmonic V2 row 21 | 0.1% | 3
| 2427 | 97B | 1 | Harmonic V3 row 21 | 0.1% | 3
| 2428 | 97C | 1 | Harmonic V1 row 23 | 0.1% | 3
| 2429 | 97D | 1 | Harmonic V2 row 23 | 0.1% | 3
| 2430 | 97E | 1 | Harmonic V3 row 23 | 0.1% | 3
| 2431 | 97F | 1 | Harmonic V1 row 25 | 0.1% | 3
| 2432 | 980 | 1 | Harmonic V2 row 25 | 0.1% | 3
| 2433 | 981 | 1 | Harmonic V3 row 25 | 0.1% | 3
| 2304 | 900 | 130
100 Hex : Option
| Address Dec. | Address Hex. | Word Count | Description | Unit | Function
| 256 | 100 | 1 | Product Option Code |  | 3
| 257 | 101 | 1 | Constructor code |  | 3
| 258 | 102 | 1 | Option slot 1 0xFF : None 0x0 : communication option 0x1 : Metering option 0x03 : Metering + Harmonics option 0xF0 : Neutral curent option 0x20 : Input/Output option 0x30 : Analog Outputs option 0x40 : Memory option 0x50 : Proﬁbus option 0x60 : Temperature option 0x70 : Ethernet option |  | 3
| 259 | 103 | 1 | Option slot 2 |  | 3
| 260 | 104 | 1 | Option slot 3 |  | 3
| 261 | 105 | 1 | Option slot 4 |  | 3
| 262 | 106 | 1 | Software version |  | 3
| 263 | 107 | 4 | Serial number |  | 3
| 256 | 100 | 11
200 Hex : Settings
| Address Dec. | Address Hex. | Word Count | Description | Unit | Function
| 512 | 200 | 1 | Network Type : 0 : 1BL 1 : 2BL 2 : 3BL 3 : 3NBL 4 : 4BL 5 : 4NBL 6 : 2NBL | / | 3,6,16
| 513 | 201 | 1 | Current Transformer secondary : 1: 1 A 5: 5 A | A | 3,6,16
| 514 | 202 | 1 | Current Transformer primary | A | 3,6,16
| 515 | 203 | 1 | Voltage transformer present : 0 : No 1: Yes |  | 3,6,16
| 516 | 204 | 2 | Voltage Transformersecondary : 60 : 60 V 100 : 100 V 110 : 110 V 115 : 115 V 120 : 120 V 173 : 173 V 190 : 190 V |  | 3,6,16
| 518 | 206 | 1 | Voltage Transformer primary |  | 3,6,16
| 519 | 207 | 1 | Synchronisation of I AVG/MAX: 2 : 2 seconds 10 : 10 seconds 300 : 5 minutes 480 : 8 minutes 600 : 10 Minutes 900 : 15 minutes 1200 : 20 minutes 1800 : 30 minutes 3600 : 60 minutes | s | 3,6,16
| 520 | 208 | 1 | Synchronisation of P/Q/S AVG/MAX 10 : 10 seconds 300 : 5 minutes 480 : 8 minutes 600 : 10 Minutes 900 : 15 minutes 1200 : 20 minutes 1800 : 30 minutes 3600 : 60 minutes | / | 3,6,16
| 521 | 209 | 1 | OUT 1 : pulse output allocation : 0 : Ea+ 1 : Er+ 2 : Es 3 : Ea- 4 : Er- | / | 3,6,16
| 522 | 20A | 1 | OUT 1 : pulse output value : 0 : 0,1 kWh/kvarh 1 : 1 kWh/kvarh 2 : 10 kWh/kvarh 3 : 100 kWh/kvarh 4 : 1000 kWh/kvarh 5 : 10000 kWh/kvarh |  | 3,6,16
| 523 | 20B | 1 | OUT 1 : pulse output duration : 1 : 100ms 2 : 200ms 3 : 300ms 4 : 400ms 5 : 500ms 6 : 600ms 7 : 700ms 8 : 800ms 9 : 900ms |  | 3,6,16
| 524 | 20C | 1 | OUT 2 : pulse output allocation : 0 : Ea+ 1 : Er+ 2 : Es 3 : Ea- 4 : Er- |  | 3,6,16
| 525 | 20D | 1 | OUT 2 : pulse output value : 0 : 0,1 kWh/kvarh/kVAh 1 : 1 kWh/kvarh/kVAh 2 : 10 kWh/kvarh/kVAh 3 : 100 kWh/kvarh/kVAh 4 : 1000 kWh/kvarh/kVAh 5 : 10000 kWh/kvarh/kVAh |  | 3,6,16
| 526 | 20E | 1 | OUT 2 : pulse output duration : 1 : 100 ms 2 : 200 ms 3 : 300 ms 4 : 400 ms 5 : 500 ms 6 : 600 ms 7 : 700 ms 8 : 800 ms 9 : 900 ms |  | 3,6,16
| 527 | 20F | 1 | Type of analog output OUT 1 : 0 : 0/20 mA 1 : 4/20 mA 2 : 30 V |  | 3,6,16
| 528 | 210 | 1 | Output allocation analog OUT1 : 0: I1 1: I2 2: I3 3: In 4: U12 5: U23 6: U31 7: ∑P 8: ∑Q 9: ∑S 10 : ∑PFL 11 : V1 12 : V2 13 : V3 14 : F 15 : ∑PFC 16 : I Sys 17 : U Sys 18 : V Sys 19 : ∑P predicted 20 : ∑Q Precdicted 21 : ∑S predicted 22 : T°C 1 23 : T°C 2 24 : T°C 3 25 : T°C internal |  | 3,6,16
| 529 | 211 | 1 | Value at 0 or 4 mA from analog output OUT 1 |  | 3,6,16
| 530 | 212 | 1 | Unit at 0 or 4 mA from analog output OUT1 0: / 1 : k 2: M |  | 3,6,16
| 531 | 213 | 1 | Value at 20 mA from analog output OUT 1 |  | 3,6,16
| 532 | 214 | 1 | Unit at 20 mA from analog output OUT1 0: / 1 : k 2: M |  | 3,6,16
| 533 | 215 | 1 | Type of analog output OUT 2 : 0 : 0/20 mA 1 : 4/20 mA 2 : 30 V |  | 3,6,16
| 534 | 216 | 1 | Output allocation analog OUT2 : 0: I1 1: I2 2: I3 3: In 4: U12 5: U23 6: U31 7: ∑P 8: ∑Q 9: ∑S 10 : ∑PFL 11 : V1 12 : V2 13 : V3 14 : F 15 : ∑PFC 16 : I Sys 17 : U Sys 18 : V Sys 19 : ∑P predicted 20 : ∑Q Precdicted 21 : ∑S predicted 22 : T°C 1 23 : T°C 2 24 : T°C 3 25 : T°C internal |  | 3,6,16
| 535 | 217 | 1 | Value at 0 or 4 mA from analog output OUT 2 |  | 3,6,16
| 536 | 218 | 1 | Unit at 0 or 4 mA from analog output OUT2 0: / 1 : k 2: M |  | 3,6,16
| 537 | 219 | 1 | Value at 20 mA from analog output OUT 2 |  | 3,6,16
| 538 | 21A | 1 | Unit at 20 mA from analog output OUT2 0: / 1 : k 2: M |  | 3,6,16
| 539 | 21B | 1 | Type of analog output OUT 3 : 0 : 0/20 mA 1 : 4/20 mA 2 : 30 V |  | 3,6,16
| 540 | 21C | 1 | Output allocation analog OUT 3 : 0: I1 1: I2 2: I3 3: In 4: U12 5: U23 6: U31 7: ∑P 8: ∑Q 9: ∑S 10 : ∑PFL 11 : V1 12 : V2 13 : V3 14 : F 15 : ∑PFC 16 : I Sys 17 : U Sys 18 : V Sys 19 : ∑P predicted 20 : ∑Q Precdicted 21 : ∑S predicted 22 : T°C 1 23 : T°C 2 24 : T°C 3 25 : T°C internal |  | 3,6,16
| 541 | 21D | 1 | Value at 0 or 4 mA from analog output OUT 3 |  | 3,6,16
| 542 | 21E | 1 | Unit at 0 or 4 mA from analog output OUT 3 0: / 1 : k 2: M |  | 3,6,16
| 543 | 21F | 1 | Value at 20 mA from analog output OUT 3 |  | 3,6,16
| 544 | 220 | 1 | Unit at 20 mA from analog output OUT 3 0: / 1 : k 2: M |  | 3,6,16
| 545 | 221 | 1 | Type of analog output OUT 4 : 0 : 0/20 mA 1 : 4/20 mA 2 : 30 V |  | 3,6,16
| 546 | 222 | 1 | Output allocation analog OUT 4 : 0: I1 1: I2 2: I3 3: In 4: U12 5: U23 6: U31 7: ∑P 8: ∑Q 9: ∑S 10 : ∑PFL 11 : V1 12 : V2 13 : V3 14 : F 15 : ∑PFC 16 : I Sys 17 : U Sys 18 : V Sys 19 : ∑P predicted 20 : ∑Q Precdicted 21 : ∑S predicted 22 : T°C 1 23 : T°C 2 24 : T°C 3 25 : T°C internal |  | 3,6,16
| 547 | 223 | 1 | Value at 0 or 4 mA from analog output OUT 4 |  | 3,6,16
| 548 | 224 | 1 | Unit at 0 or 4 mA from analog output OUT 4 0: / 1 : k 2: M |  | 3,6,16
| 549 | 225 | 1 | Value at 20 mA from analog output OUT 4 |  | 3,6,16
| 550 | 226 | 1 | Unit at 20 mA from analog output OUT 4 0: / 1 : k 2: M |  | 3,6,16
| 551 | 227 | 1 | relay OUT 1 Allocation : 0 : Cde 1: I 2: U 3: ∑P + 4: ∑Q + 5: ∑S 6: F 7 : ∑PFL 8 : thd 3I 9 : thd 3U 10 : IN 11 : Hour 12 : V 13 : thd In 14 : thd 3V 15 : ∑P - 16 : ∑Q - 17 : ∑PFC 18 : Cd-t 19 : T°C 1 20 : T°C 2 21 : T°C 3 22 : T°C internal 23 : ∑P predicted 24 : ∑Q Precdicted 25 : ∑S predicted |  | 3,6,16
| 552 | 228 | 1 | Lower Threshold OUT 1 |  | 3,6,16
| 553 | 229 | 1 | Unit lower threshold OUT 1 0: / 1: k 2: M |  | 3,6,16
| 554 | 22A | 1 | Upper Threshold OUT 1 |  | 3,6,16
| 555 | 22B | 1 | Unit upper threshold OUT 1 0: / 1: k 2: M |  | 3,6,16
| 556 | 22C | 1 | Hysteresis 0 to 99 OUT 1 |  | 3,6,16
| 557 | 22D | 1 | Specified time OUT 1 |  | 3,6,16
| 558 | 22E | 1 | Relay status OUT 1 : 0 : Open 1 : Closed |  | 3,6,16
| 559 | 22F | 1 | relay OUT 2 Allocation : 0 : Cde 1: I 2: U 3: ∑P + 4: ∑Q + 5: ∑S 6: F 7 : ∑PFL 8 : thd 3I 9 : thd 3U 10 : IN 11 : Hour 12 : V 13 : thd In 14 : thd 3V 15 : ∑P - 16 : ∑Q - 17 : ∑PFC 18 : Cd-t 19 : T°C 1 20 : T°C 2 21 : T°C 3 22 : T°C internal 23 : ∑P predicted 24 : ∑Q Precdicted 25 : ∑S predicted |  | 3,6,16
| 560 | 230 | 1 | Lower Threshold OUT 2 |  | 3,6,16
| 561 | 231 | 1 | Unit lower threshold OUT 2 0: / 1: k 2: M |  | 3,6,16
| 562 | 232 | 1 | Upper Threshold OUT 2 |  | 3,6,16
| 563 | 233 | 1 | Unit upper threshold OUT 2 0: / 1: k 2: M |  | 3,6,16
| 564 | 234 | 1 | Hysteresis 0 to 99 OUT 2 |  | 3,6,16
| 565 | 235 | 1 | Specified time OUT 2 |  | 3,6,16
| 566 | 236 | 1 | Relay status OUT 2 0 : Open 1 : Closed |  | 3,6,16
| 567 | 237 | 1 | Reserve constructor |  | 3,6,16
| 568 | 238 | 1 | Reserve constructor |  | 3,6,16
| 569 | 239 | 1 | Reserve constructor |  | 3,6,16
| 570 | 23A | 1 | Reserve constructor |  | 3,6,16
| 571 | 23B | 1 | Neutral current transformer secondary: 1: 1 A 5: 5 A |  | 3,6,16
| 572 | 23C | 1 | Neutral current transformer primary |  | 3,6,16
| 573 | 23D | 1 | Synchronisation of U AVG/MAX 10 : 10 seconds 300 : 5 minutes 480 : 8 minutes 600 : 10 Minutes 900 : 15 minutes 1200 : 20 minutes 1800 : 30 minutes 3600 : 60 minutes |  | 3,6,16
| 574 | 23E | 1 | Synchronisation of F AVG/MAX 10 : 10 seconds 300 : 5 minutes 480 : 8 minutes 600 : 10 Minutes 900 : 15 minutes 1200 : 20 minutes 1800 : 30 minutes 3600 : 60 minutes |  | 3,6,16
| 575 | 23F | 1 | Mean power memory storage P+ : 0: NO / 1: YES |  | 3,6,16
| 576 | 240 | 1 | Mean power memory storage P- : 0: NO / 1: YES |  | 3,6,16
| 577 | 241 | 1 | Mean power memory storage Q+ : 0: NO / 1: YES |  | 3,6,16
| 578 | 242 | 1 | Mean power memory storage Q- : 0: NO / 1: YES |  | 3,6,16
| 579 | 243 | 1 | Mean power synchronization signal : 0: internal 1: external |  | 3,6,16
| 580 | 244 | 1 | Synchronization period for P+,P-,Q+,Q- : 300 : 5 minutes 480 : 8 minutes 600 : 10 Minutes 900 : 15 minutes 1200 : 20 minutes 1800 : 30 minutes |  | 3,6,16
| 581 | 245 | 1 | relay OUT 3 Allocation : 0 : Cde 1: I 2: U 3: ∑P + 4: ∑Q + 5: ∑S 6: F 7 : ∑PFL 8 : thd 3I 9 : thd 3U 10 : IN 11 : Hour 12 : V 13 : thd In 14 : thd 3V 15 : ∑P - 16 : ∑Q - 17 : ∑PFC 18 : Cd-t 19 : T°C 1 20 : T°C 2 21 : T°C 3 22 : T°C internal 23 : ∑P predicted 24 : ∑Q Precdicted 25 : ∑S predicted |  | 3,6,16
| 582 | 246 | 1 | Lower Threshold OUT 3 |  | 3,6,16
| 583 | 247 | 1 | Unit lower threshold OUT 3 0: / 1: k 2: M |  | 3,6,16
| 584 | 248 | 1 | Upper Threshold OUT 3 |  | 3,6,16
| 585 | 249 | 1 | Unit upper threshold OUT 3 0: / 1: k 2: M |  | 3,6,16
| 586 | 24A | 1 | Hysteresis 0 to 99 OUT 3 |  | 3,6,16
| 587 | 24B | 1 | Specified time OUT 3 |  | 3,6,16
| 588 | 24C | 1 | Relay status OUT 3 : 0 : Open 1 : Closed |  | 3,6,16
| 589 | 24D | 1 | relay OUT 4 Allocation : 0 : Cde 1: I 2: U 3: ∑P + 4: ∑Q + 5: ∑S 6: F 7 : ∑PFL 8 : thd 3I 9 : thd 3U 10 : IN 11 : Hour 12 : V 13 : thd In 14 : thd 3V 15 : ∑P - 16 : ∑Q - 17 : ∑PFC 18 : Cd-t 19 : T°C 1 20 : T°C 2 21 : T°C 3 22 : T°C internal 23 : ∑P predicted 24 : ∑Q Precdicted 25 : ∑S predicted |  | 3,6,16
| 590 | 24E | 1 | Lower Threshold OUT 4 |  | 3,6,16
| 591 | 24F | 1 | Unit lower threshold OUT 4 0: / 1: k 2: M |  | 3,6,16
| 592 | 250 | 1 | Upper Threshold OUT 4 |  | 3,6,16
| 593 | 251 | 1 | Unit upper threshold OUT 4 0: / 1: k 2: M |  | 3,6,16
| 594 | 252 | 1 | Hysteresis 0 to 99 OUT 4 |  | 3,6,16
| 595 | 253 | 1 | Specified time OUT 4 |  | 3,6,16
| 596 | 254 | 1 | Relay status OUT 4 0 : Open 1 : Closed |  | 3,6,16
| 597 | 255 | 1 | relay OUT 5 Allocation : 0 : Cde 1: I 2: U 3: ∑P + 4: ∑Q + 5: ∑S 6: F 7 : ∑PFL 8 : thd 3I 9 : thd 3U 10 : IN 11 : Hour 12 : V 13 : thd In 14 : thd 3V 15 : ∑P - 16 : ∑Q - 17 : ∑PFC 18 : Cd-t 19 : T°C 1 20 : T°C 2 21 : T°C 3 22 : T°C internal 23 : ∑P predicted 24 : ∑Q Precdicted 25 : ∑S predicted |  | 3,6,16
| 598 | 256 | 1 | Lower Threshold OUT 5 |  | 3,6,16
| 599 | 257 | 1 | Unit lower threshold OUT 5 0: / 1: k 2: M |  | 3,6,16
| 600 | 258 | 1 | Upper Threshold OUT 5 |  | 3,6,16
| 601 | 259 | 1 | Unit upper threshold OUT 5 0: / 1: k 2: M |  | 3,6,16
| 602 | 25A | 1 | Hysteresis 0 to 99 OUT 5 |  | 3,6,16
| 603 | 25B | 1 | Specified time OUT 5 |  | 3,6,16
| 604 | 25C | 1 | Relay status OUT 5 0 : Open 1 : Closed |  | 3,6,16
| 605 | 25D | 1 | relay OUT 6 Allocation : 0 : Cde 1: I 2: U 3: ∑P + 4: ∑Q + 5: ∑S 6: F 7 : ∑PFL 8 : thd 3I 9 : thd 3U 10 : IN 11 : Hour 12 : V 13 : thd In 14 : thd 3V 15 : ∑P - 16 : ∑Q - 17 : ∑PFC 18 : Cd-t 19 : T°C 1 20 : T°C 2 21 : T°C 3 22 : T°C internal 23 : ∑P predicted 24 : ∑Q Precdicted 25 : ∑S predicted |  | 3,6,16
| 606 | 25E | 1 | Lower Threshold OUT 6 |  | 3,6,16
| 607 | 25F | 1 | Unit lower threshold OUT 6 0: / 1: k 2: M |  | 3,6,16
| 608 | 260 | 1 | Upper Threshold OUT 6 |  | 3,6,16
| 609 | 261 | 1 | Unit upper threshold OUT 6 0: / 1: k 2: M |  | 3,6,16
| 610 | 262 | 1 | Hysteresis 0 to 99 OUT 6 |  | 3,6,16
| 611 | 263 | 1 | Specified time OUT 6 |  | 3,6,16
| 612 | 264 | 1 | Relay status OUT 6 0 : Open 1 : Closed |  | 3,6,16
| 613 | 265 | 1 | Voltage dips detection threshold (SAG) | % | 3,6,16
| 614 | 266 | 1 | Voltage dips detection threshold hysteresis (SAG) | % | 3,6,16
| 615 | 267 | 1 | Voltage surge detection threshold (SWELL) | % | 3,6,16
| 616 | 268 | 1 | Voltage surge detection threshold hysteresis (SWELL) | % | 3,6,16
| 617 | 269 | 1 | Hour meter allocation 1 : Auxiliary power supply 2 : Currents 3 : phase to phase voltage |  | 3,6,16
| 618 | 26A | 1 | Hour meter trigger threshold | A/V | 3,6,16
| 619 | 26B | 1 | Réserve Constructeur |  | 3,6,16
| 512 | 200 | 108
To validate the modification, it's necessary to "Reset" the product see table 600Hex "Steup storage and Reset"
400 Hex : Reset to zero ( These values could be combine all )
| Address Dec. | Address Hex. | Word Count | Description | Unit | Function
| 1024 | 400 | 1 | Reset: Max3I : 0x1 MaxP+ : 0x2 MaxP-: 0x4 MaxQ+ : 0x8 MaxQ-: 0x10 MaxS : 0x20 Hour Meter : 0x40 kWh+ : 0x80 kvarh+ : 0x100 kVAh : 0x200 kWh-: 0x400 kvarh-: 0x800 All parameters: 0x1000 MaxU : 0x2000 MaxV : 0x4000 MaxF : 0x8000 | / | 6.16
| 1025 | 401 | 1 | Reset : E1 : 0x1 E2 : 0x2 E3 : 0x4 E4 : 0x8 E5 : 0x10 E6 : 0x20 Min/Max I : 0x40 Min/Max In : 0x80 Min/Max U : 0x100 Min/Max F : 0x200 Min/Max PF : 0x400 Min/Max P : 0x800 Min/Max Q : 0x1000 Min/Max thd I : 0x2000 Min/Max thd In : 0x4000 Min/Max thd U : 0x8000 |  | 6.16
| 1026 | 402 | 1 | Reset : Min/Max S : 0x0001 Min/Max V : 0x0002 Min/Max thd V : 0x0004 External input ( Memoru option ) : 0x0008 10 Last Alarms historic : 0x0010 10 Last voltage sag historic : 0x0020 10 Last voltage swell historic : 0x0040 10 Last voltage cut off historic : 0x0080 Frenquency Average historic : 0x2000 Voltage Average historic : 0x4000 Power Average historic : 0x8000 |  | 6.16
| 1024 | 400 | 3
500 Hex : Alarme
OUTPUT 1 : Alarme
| Address Dec. | Address Hex. | Word Count | Description | Unit | Function
| 1280 | 500 | 1 | OUT1: Current alarm on lower threshold cause: 0 : No Alarm / 1 : I1 / 2 : I2 / 3 : I3 / 4 : IN / 5 : U12 / 6 : U23 / 7 : U31 / 8 : ∑P+ / 9 : ∑Q+ / 10 : ∑S / 11 : F / 12 : ∑PFL / 15: thdI1 / 16: thdI2 / 17 : thdI3 / 18 : thdU12 / 19 : thdU23 / 20 : thdU31 / 21 : Hour / 22: V1 / 23 : V2 / 24 : V3 / 25 : thdIn 26: thdV1 / 27 : thdV2 / 28 : thd V3 / 29 : ∑P - / 30 : ∑Q - / 31 : ∑PFC / 32 : T°C 1 / 33 : T°C 2 / 34 : T°C 3 / 35 : T°C internal / 36 : ∑P predicted / 37 : ∑Q predicted / 38 : ∑S predicted | 0 : - 1 / 2 / 3 / 4 : mA 5 / 6 / 7 : mV 8 : mW 9 : mVAr 10 : mVA 11 : Hz/1000 12 : - 15 / 16 / 17 : /1000 18 / 19 / 20 : /1000 21 : Hour/100 22 / 23 / 24 : mV 25 : /1000 26 / 27 / 28 : /1000 31: - 32 / 33 / 34 / 35 : °C/10 36 : mW 37 : mVAr 38 : mVA | 3
| 1281 | 501 | 2 | OUT1: Current alarm on lower threshold : min value | - | 3
| 1283 | 503 | 1 | OUT1: Current alarm on upper threshold cause: 0 : No Alarm / 1 : I1 / 2 : I2 / 3 : I3 / 4 : IN / 5 : U12 / 6 : U23 / 7 : U31 / 8 : ∑P+ / 9 : ∑Q+ / 10 : ∑S / 11 : F / 12 : ∑PFL / 15: thdI1 / 16: thdI2 / 17 : thdI3 / 18 : thdU12 / 19 : thdU23 / 20 : thdU31 / 21 : Hour / 22: V1 / 23 : V2 / 24 : V3 / 25 : thdIn 26: thdV1 / 27 : thdV2 / 28 : thd V3 / 29 : ∑P - / 30 : ∑Q - / 31 : ∑PFC / 32 : T°C 1 / 33 : T°C 2 / 34 : T°C 3 / 35 : T°C internal / 36 : ∑P predicted / 37 : ∑Q predicted / 38 : ∑S predicted | 0 : - 1 / 2 / 3 / 4 : mA 5 / 6 / 7 : mV 8 : mW 9 : mVAr 10 : mVA 11 : Hz/1000 12 : - 15 / 16 / 17 : /1000 18 / 19 / 20 : /1000 21 : Hour/100 22 / 23 / 24 : mV 25 : /1000 26 / 27 / 28 : /1000 31: - 32 / 33 / 34 / 35 : °C/10 36 : mW 37 : mVAr 38 : mVA | 3
| 1284 | 504 | 2 | OUT1: Current alarm on upper threshold : max value | - | 3
| 1286 | 506 | 1 | OUT1: Current alarm duration | s | 3
| 1287 | 507 | 1 | OUT1: Previous (n-1) alarm on lower threshold cause | / (same as @500) | 3
| 1288 | 508 | 2 | OUT1: Previous (n-1) alarm on lower threshold min value | / | 3
| 1290 | 50A | 1 | OUT1: Previous (n-1) alarm on upper threshold cause | / (same as @503) | 3
| 1291 | 50B | 2 | OUT1: Previous (n-1) alarm on upper threshold max value | / | 3
| 1293 | 50D | 1 | OUT1: Previous (n-1) alarm duration | s | 3
| 1294 | 50E | 1 | OUT1: Previous (n-2) alarm on lower threshold cause | / (same as @500) | 3
| 1295 | 50F | 2 | OUT1: Previous (n-2) alarm on lower threshold min value | / | 3
| 1297 | 511 | 1 | OUT1: Previous (n-2) alarm on upper threshold cause | / (same as @503) | 3
| 1298 | 512 | 2 | OUT1: Previous (n-2) alarm on upper threshold max value | / | 3
| 1300 | 514 | 1 | OUT1: Previous (n-2) alarm duration | s | 3
| 1301 | 515 | 1 | OUT1: Previous (n-3) alarm on lower threshold cause | / (same as @500) | 3
| 1302 | 516 | 2 | OUT1: Previous (n-3) alarm on lower threshold min value | / | 3
| 1304 | 518 | 1 | OUT1: Previous (n-3) alarm on upper threshold cause | / (same as @503) | 3
| 1305 | 519 | 2 | OUT1: Previous (n-3) alarm on upper threshold max value | / | 3
| 1307 | 51B | 1 | OUT1: Previous (n-3) alarm duration | s | 3
OUTPUT 2 : Alarme
| 1308 | 51C | 28 | Same description like the OUTPUT 1
| 1336 | 538 | 1 | status inputs 1,2,3, 4, 5, 6 | – | 3
OUTPUT 3 : Alarme
| 1337 | 539 | 7 | Same description like the Current Alarm OUT 1 |  | 3
OUTPUT 4 : Alarme
| 1344 | 540 | 7 | Same description like the Current Alarm OUT 1 |  | 3
OUTPUT 5 : Alarme
| 1351 | 547 | 7 | Same description like the Current Alarm OUT 1 |  | 3
OUTPUT 6 : Alarme
| 1358 | 54E | 7 | Same description like the Current Alarm OUT 1 |  | 3
| 1280 | 500 | 85
600 Hex : Setup storage and Reset product ( Function 6 )
| Address Dec. | Address Hex. | Word Count | Description | Unit | Function
| 1536 | 600 | 1 | No parameter |  | 6
A00 Hex : Pulse meters values
| Address Dec. | Address Hex. | Word Count | Description | Unit | Function
| 2560 | A00 | 2 | input E1 Option ES1 |  | 3
| 2562 | A02 | 2 | input E2 Option ES1 |  | 3
| 2564 | A04 | 2 | input E3 Option ES2 |  | 3
| 2566 | A06 | 2 | input E4 Option ES2 |  | 3
| 2568 | A08 | 2 | input E5 Option ES3 |  | 3
| 2570 | A0A | 2 | input E6 Option ES3 |  | 3
| 2560 | A00 | 12
C00 Hex : Date and Hour Settings
| Address Dec. | Address Hex. | Word Count | Description | Unit | Function
| 3072 | C00 | 1 | Day |  | 3.16
| 3073 | C01 | 1 | Month |  | 3.16
| 3074 | C02 | 1 | Year |  | 3.16
| 3075 | C03 | 1 | Hour |  | 3.16
| 3076 | C04 | 1 | Minute |  | 3.16
| 3077 | C05 | 1 | Second |  | 3.16
| 3072 | C00 | 6
To write the date and hour, it's only possible in one operation ( Function 16 with 6 words )
C10 Hex :Last 10 Alarms event log
| Address Dec. | Address Hex. | Word Count | Description | Unit | Function
Alarm Level n-1
| 3088 | C10 | 1 | Alarm Output number (1 à 6) |  | 3
| 3089 | C11 | 1 | Alarm on lower threshold cause: 0 : No Alarm / 1 : I1 / 2 : I2 / 3 : I3 / 4 : IN / 5 : U12 / 6 : U23 / 7 : U31 / 8 : ∑P+ / 9 : ∑Q+ / 10 : ∑S / 11 : F / 12 : ∑PFL / 15: thdI1 / 16: thdI2 / 17 : thdI3 / 18 : thdU12 / 19 : thdU23 / 20 : thdU31 / 21 : Hour / 22: V1 / 23 : V2 / 24 : V3 / 26: thdV1 / 27 : thdV2 / 28 : thd V3 / 29 : ∑P - / 30 : ∑Q - / 31 : ∑PFC / 32 : T°C 1 / 33 : T°C 2 / 34 : T°C 3 / 35 : T°C internal / 36 : ∑P predicted / 37 : ∑Q predicted / 38 : ∑S predicted | 0 : - 1 / 2 / 3 / 4 : mA 5 / 6 / 7 : mV 8 : mW 9 : mVAr 10 : mVA 11 : Hz/1000 12 : - 15 / 16 / 17 : /1000 18 / 19 / 20 : /1000 21 : Hour/100 22 / 23 / 24 : mV 26 / 27 / 28 : /1000 31: - 32 / 33 / 34 / 35 : °C/10 36 : mW 37 : mVAr 38 : mVA | 3
| 3090 | C12 | 2 | Alarm on lower threshold : min value | - | 3
| 3092 | C14 | 1 | Alarm on upper threshold cause: 0 : No Alarm / 1 : I1 / 2 : I2 / 3 : I3 / 4 : IN / 5 : U12 / 6 : U23 / 7 : U31 / 8 : ∑P+ / 9 : ∑Q+ / 10 : ∑S / 11 : F / 12 : ∑PFL / 15: thdI1 / 16: thdI2 / 17 : thdI3 / 18 : thdU12 / 19 : thdU23 / 20 : thdU31 / 21 : Hour / 22: V1 / 23 : V2 / 24 : V3 / 26: thdV1 / 27 : thdV2 / 28 : thd V3 / 29 : ∑P - / 30 : ∑Q - / 31 : ∑PFC / 32 : T°C 1 / 33 : T°C 2 / 34 : T°C 3 / 35 : T°C internal / 36 : ∑P predicted / 37 : ∑Q predicted / 38 : ∑S predicted | 0 : - 1 / 2 / 3 / 4 : mA 5 / 6 / 7 : mV 8 : mW 9 : mVAr 10 : mVA 11 : Hz/1000 12 : - 15 / 16 / 17 : /1000 18 / 19 / 20 : /1000 21 : Hour/100 22 / 23 / 24 : mV 26 / 27 / 28 : /1000 31: - 32 / 33 / 34 / 35 : °C/10 36 : mW 37 : mVAr 38 : mVA | 3
| 3093 | C15 | 2 | Alarm on upper threshold : max value | - | 3
| 3095 | C17 | 1 | duration |  | 3
| 3096 | C18 | 1 | Month |  | 3
| 3097 | C19 | 1 | Day |  | 3
| 3098 | C1A | 1 | Year |  | 3
| 3099 | C1B | 1 | Hour |  | 3
| 3100 | C1C | 1 | Minute |  | 3
| 3101 | C1D | 1 | Seconde |  | 3
Alarm Level n-2
| 3102 | C1E | 14 | See description level n-1 |  | 3
Alarm Level n-3
| 3116 | C2C | 14 | See description level n-1 |  | 3
Alarm Level n-4
| 3130 | C3A | 14 | See description level n-1 |  | 3
Alarm Level n-5
| 3144 | C48 | 14 | See description level n-1 |  | 3
Alarm Level n-6
| 3158 | C56 | 14 | See description level n-1 |  | 3
Alarm Level n-7
| 3172 | C64 | 14 | See description level n-1 |  | 3
Alarm Level n-8
| 3186 | C72 | 14 | See description level n-1 |  | 3
Alarm Level n-9
| 3200 | C80 | 14 | See description level n-1 |  | 3
Alarm Level n-10
| 3214 | C8E | 14 | See description level n-1 |  | 3
| 3088 | C10 | 140
D00 Hex : Last 10 Voltage dips event log / SAG
| Address Dec. | Address Hex. | Word Count | Description | Unit | Function
Voltage Sag Level n-1
| 3328 | D00 | 1 | Root cause on phase to phase voltage 0 : aucune, 5: U12, 6: U23, 7: U31 |  | 3
| 3329 | D01 | 2 | Value |  | 3
| 3331 | D03 | 1 | Root cause on phase to neutral voltage 0 : aucune, 22 : V1, 23 : V2, 24 : V3 |  | 3
| 3332 | D04 | 2 | Value |  | 3
| 3334 | D06 | 2 | Duration |  | 3
| 3336 | D08 | 1 | Month |  | 3
| 3337 | D09 | 1 | Day |  | 3
| 3338 | D0A | 1 | Year |  | 3
| 3339 | D0B | 1 | Hour |  | 3
| 3340 | D0C | 1 | Minute |  | 3
| 3341 | D0D | 1 | Second |  | 3
Voltage Sag Level n-2
| 3342 | D0E | 14 | See description level n-1 |  | 3
Voltage Sag Level n-2
| 3356 | D1C | 14 | See description level n-1 |  | 3
Voltage Sag Level n-2
| 3370 | D2A | 14 | See description level n-1 |  | 3
Voltage Sag Level n-2
| 3384 | D38 | 14 | See description level n-1 |  | 3
Voltage Sag Level n-2
| 3398 | D46 | 14 | See description level n-1 |  | 3
Voltage Sag Level n-2
| 3412 | D54 | 14 | See description level n-1 |  | 3
Voltage Sag Level n-2
| 3426 | D62 | 14 | See description level n-1 |  | 3
Voltage Sag Level n-2
| 3440 | D70 | 14 | See description level n-1 |  | 3
Voltage Sag Level n-2
| 3454 | D7E | 14 | See description level n-1 |  | 3
| 3328 | D00 | 140
E00 Hex : Last 10 Voltage surge event log / SWELL
| Address Dec. | Address Hex. | Word Count | Description | Unit | Function
Voltage Swell Level n-1
| 3584 | E00 | 1 | Root cause on phase to phase voltage 0 : aucune, 5: U12, 6: U23, 7: U31 |  | 3
| 3585 | E01 | 2 | Value |  | 3
| 3587 | E03 | 1 | Root cause on phase to neutral voltage 0 : aucune, 22 : V1, 23 : V2, 24 : V3 |  | 3
| 3588 | E04 | 2 | Value |  | 3
| 3590 | E06 | 2 | Duration |  | 3
| 3592 | E08 | 1 | Month |  | 3
| 3593 | E09 | 1 | Day |  | 3
| 3594 | E0A | 1 | Year |  | 3
| 3595 | E0B | 1 | Hour |  | 3
| 3596 | E0C | 1 | Minute |  | 3
| 3597 | E0D | 1 | Second |  | 3
Voltage Swell Level n-2
| 3598 | E0E | 14 | See description level n-1 |  | 3
Voltage Swell Level n-2
| 3612 | E1C | 14 | See description level n-1 |  | 3
Voltage Swell Level n-2
| 3626 | E2A | 14 | See description level n-1 |  | 3
Voltage Swell Level n-2
| 3640 | E38 | 14 | See description level n-1 |  | 3
Voltage Swell Level n-2
| 3654 | E46 | 14 | See description level n-1 |  | 3
Voltage Swell Level n-2
| 3668 | E54 | 14 | See description level n-1 |  | 3
Voltage Swell Level n-2
| 3682 | E62 | 14 | See description level n-1 |  | 3
Voltage Swell Level n-2
| 3696 | E70 | 14 | See description level n-1 |  | 3
Voltage Swell Level n-2
| 3710 | E7E | 14 | See description level n-1 |  | 3
| 3584 | E00 | 140
F00 Hex : Minimum and Maximum Instantanious value
| Address Dec. | Address Hex. | Word Count | Description | Unit | Function
| 3840 | F00 | 2 | 3I Minimum |  | 3
| 3842 | F02 | 1 | Month |  | 3
| 3843 | F03 | 1 | Day |  | 3
| 3844 | F04 | 1 | Year |  | 3
| 3845 | F05 | 1 | Hour |  | 3
| 3846 | F06 | 1 | Minute |  | 3
| 3847 | F07 | 1 | Second |  | 3
| 3848 | F08 | 2 | 3I Maximum |  | 3
| 3850 | F0A | 1 | Month |  | 3
| 3851 | F0B | 1 | Day |  | 3
| 3852 | F0C | 1 | Year |  | 3
| 3853 | F0D | 1 | Hour |  | 3
| 3854 | F0E | 1 | Minute |  | 3
| 3855 | F0F | 1 | Second |  | 3
| 3856 | F10 | 2 | IN Minimum |  | 3
| 3858 | F12 | 1 | Month |  | 3
| 3859 | F13 | 1 | Day |  | 3
| 3860 | F14 | 1 | Year |  | 3
| 3861 | F15 | 1 | Hour |  | 3
| 3862 | F16 | 1 | Minute |  | 3
| 3863 | F17 | 1 | Second |  | 3
| 3864 | F18 | 2 | In Maximum |  | 3
| 3866 | F1A | 1 | Month |  | 3
| 3867 | F1B | 1 | Day |  | 3
| 3868 | F1C | 1 | Year |  | 3
| 3869 | F1D | 1 | Hour |  | 3
| 3870 | F1E | 1 | Minute |  | 3
| 3871 | F1F | 1 | Second |  | 3
| 3872 | F20 | 2 | 3U Minimum |  | 3
| 3874 | F22 | 1 | Month |  | 3
| 3875 | F23 | 1 | Day |  | 3
| 3876 | F24 | 1 | Year |  | 3
| 3877 | F25 | 1 | Hour |  | 3
| 3878 | F26 | 1 | Minute |  | 3
| 3879 | F27 | 1 | Second |  | 3
| 3880 | F28 | 2 | 3U Maximum |  | 3
| 3882 | F2A | 1 | Month |  | 3
| 3883 | F2B | 1 | Day |  | 3
| 3884 | F2C | 1 | Year |  | 3
| 3885 | F2D | 1 | Hour |  | 3
| 3886 | F2E | 1 | Minute |  | 3
| 3887 | F2F | 1 | Second |  | 3
| 3888 | F30 | 2 | 3V Minimum |  | 3
| 3890 | F32 | 1 | Month |  | 3
| 3891 | F33 | 1 | Day |  | 3
| 3892 | F34 | 1 | Year |  | 3
| 3893 | F35 | 1 | Hour |  | 3
| 3894 | F36 | 1 | Minute |  | 3
| 3895 | F37 | 1 | Second |  | 3
| 3896 | F38 | 2 | 3V Maximum |  | 3
| 3898 | F3A | 1 | Month |  | 3
| 3899 | F3B | 1 | Day |  | 3
| 3900 | F3C | 1 | Year |  | 3
| 3901 | F3D | 1 | Hour |  | 3
| 3902 | F3E | 1 | Minute |  | 3
| 3903 | F3F | 1 | Second |  | 3
| 3904 | F40 | 2 | F Minimum |  | 3
| 3906 | F42 | 1 | Month |  | 3
| 3907 | F43 | 1 | Day |  | 3
| 3908 | F44 | 1 | Year |  | 3
| 3909 | F45 | 1 | Hour |  | 3
| 3910 | F46 | 1 | Minute |  | 3
| 3911 | F47 | 1 | Second |  | 3
| 3912 | F48 | 2 | F Maximum |  | 3
| 3914 | F4A | 1 | Month |  | 3
| 3915 | F4B | 1 | Day |  | 3
| 3916 | F4C | 1 | Year |  | 3
| 3917 | F4D | 1 | Hour |  | 3
| 3918 | F4E | 1 | Minute |  | 3
| 3919 | F4F | 1 | Second |  | 3
| 3920 | F50 | 2 | ∑PF Minimum |  | 3
| 3922 | F52 | 1 | Month |  | 3
| 3923 | F53 | 1 | Day |  | 3
| 3924 | F54 | 1 | Year |  | 3
| 3925 | F55 | 1 | Hour |  | 3
| 3926 | F56 | 1 | Minute |  | 3
| 3927 | F57 | 1 | Second |  | 3
| 3928 | F58 | 2 | ∑PF Maximum |  | 3
| 3930 | F5A | 1 | Month |  | 3
| 3931 | F5B | 1 | Day |  | 3
| 3932 | F5C | 1 | Year |  | 3
| 3933 | F5D | 1 | Hour |  | 3
| 3934 | F5E | 1 | Minute |  | 3
| 3935 | F5F | 1 | Second |  | 3
| 3936 | F60 | 2 | ∑P+ Minimum |  | 3
| 3938 | F62 | 1 | Month |  | 3
| 3939 | F63 | 1 | Day |  | 3
| 3940 | F64 | 1 | Year |  | 3
| 3941 | F65 | 1 | Hour |  | 3
| 3942 | F66 | 1 | Minute |  | 3
| 3943 | F67 | 1 | Second |  | 3
| 3944 | F68 | 2 | ∑P+ Maximum |  | 3
| 3946 | F6A | 1 | Month |  | 3
| 3947 | F6B | 1 | Day |  | 3
| 3948 | F6C | 1 | Year |  | 3
| 3949 | F6D | 1 | Hour |  | 3
| 3950 | F6E | 1 | Minute |  | 3
| 3951 | F6F | 1 | Second |  | 3
| 3952 | F70 | 2 | ∑P- Minimum |  | 3
| 3954 | F72 | 1 | Month |  | 3
| 3955 | F73 | 1 | Day |  | 3
| 3956 | F74 | 1 | Year |  | 3
| 3957 | F75 | 1 | Hour |  | 3
| 3958 | F76 | 1 | Minute |  | 3
| 3959 | F77 | 1 | Second |  | 3
| 3960 | F78 | 2 | ∑P- Maximum |  | 3
| 3962 | F7A | 1 | Month |  | 3
| 3963 | F7B | 1 | Day |  | 3
| 3964 | F7C | 1 | Year |  | 3
| 3965 | F7D | 1 | Hour |  | 3
| 3966 | F7E | 1 | Minute |  | 3
| 3967 | F7F | 1 | Second |  | 3
| 3968 | F80 | 2 | ∑Q+ Minimum |  | 3
| 3970 | F82 | 1 | Month |  | 3
| 3971 | F83 | 1 | Day |  | 3
| 3972 | F84 | 1 | Year |  | 3
| 3973 | F85 | 1 | Hour |  | 3
| 3974 | F86 | 1 | Minute |  | 3
| 3975 | F87 | 1 | Second |  | 3
| 3976 | F88 | 2 | ∑Q+ Maximum |  | 3
| 3978 | F8A | 1 | Month |  | 3
| 3979 | F8B | 1 | Day |  | 3
| 3980 | F8C | 1 | Year |  | 3
| 3981 | F8D | 1 | Hour |  | 3
| 3982 | F8E | 1 | Minute |  | 3
| 3983 | F8F | 1 | Second |  | 3
| 3984 | F90 | 2 | ∑Q- Minimum |  | 3
| 3986 | F92 | 1 | Month |  | 3
| 3987 | F93 | 1 | Day |  | 3
| 3988 | F94 | 1 | Year |  | 3
| 3989 | F95 | 1 | Hour |  | 3
| 3990 | F96 | 1 | Minute |  | 3
| 3991 | F97 | 1 | Second |  | 3
| 3992 | F98 | 2 | ∑Q- Maximum |  | 3
| 3994 | F9A | 1 | Month |  | 3
| 3995 | F9B | 1 | Day |  | 3
| 3996 | F9C | 1 | Year |  | 3
| 3997 | F9D | 1 | Hour |  | 3
| 3998 | F9E | 1 | Minute |  | 3
| 3999 | F9F | 1 | Second |  | 3
| 4000 | FA0 | 2 | ∑S Minimum |  | 3
| 4002 | FA2 | 1 | Month |  | 3
| 4003 | FA3 | 1 | Day |  | 3
| 4004 | FA4 | 1 | Year |  | 3
| 4005 | FA5 | 1 | Hour |  | 3
| 4006 | FA6 | 1 | Minute |  | 3
| 4007 | FA7 | 1 | Second |  | 3
| 4008 | FA8 | 2 | ∑S Maximum |  | 3
| 4010 | FAA | 1 | Month |  | 3
| 4011 | FAB | 1 | Day |  | 3
| 4012 | FAC | 1 | Year |  | 3
| 4013 | FAD | 1 | Hour |  | 3
| 4014 | FAE | 1 | Minute |  | 3
| 4015 | FAF | 1 | Second |  | 3
| 4016 | FB0 | 2 | THD 3I Minimum |  | 3
| 4018 | FB2 | 1 | Month |  | 3
| 4019 | FB3 | 1 | Day |  | 3
| 4020 | FB4 | 1 | Year |  | 3
| 4021 | FB5 | 1 | Hour |  | 3
| 4022 | FB6 | 1 | Minute |  | 3
| 4023 | FB7 | 1 | Second |  | 3
| 4024 | FB8 | 2 | THD 3I Maximum |  | 3
| 4026 | FBA | 1 | Month |  | 3
| 4027 | FBB | 1 | Day |  | 3
| 4028 | FBC | 1 | Year |  | 3
| 4029 | FBD | 1 | Hour |  | 3
| 4030 | FBE | 1 | Minute |  | 3
| 4031 | FBF | 1 | Second |  | 3
| 4032 | FC0 | 2 | THD IN Minimum |  | 3
| 4034 | FC2 | 1 | Month |  | 3
| 4035 | FC3 | 1 | Day |  | 3
| 4036 | FC4 | 1 | Year |  | 3
| 4037 | FC5 | 1 | Hour |  | 3
| 4038 | FC6 | 1 | Minute |  | 3
| 4039 | FC7 | 1 | Second |  | 3
| 4040 | FC8 | 2 | THD IN Maximum |  | 3
| 4042 | FCA | 1 | Month |  | 3
| 4043 | FCB | 1 | Day |  | 3
| 4044 | FCC | 1 | Year |  | 3
| 4045 | FCD | 1 | Hour |  | 3
| 4046 | FCE | 1 | Minute |  | 3
| 4047 | FCF | 1 | Second |  | 3
| 4048 | FD0 | 2 | THD 3U Minimum |  | 3
| 4050 | FD2 | 1 | Month |  | 3
| 4051 | FD3 | 1 | Day |  | 3
| 4052 | FD4 | 1 | Year |  | 3
| 4053 | FD5 | 1 | Hour |  | 3
| 4054 | FD6 | 1 | Minute |  | 3
| 4055 | FD7 | 1 | Second |  | 3
| 4056 | FD8 | 2 | THD 3U Maximum |  | 3
| 4058 | FDA | 1 | Month |  | 3
| 4059 | FDB | 1 | Day |  | 3
| 4060 | FDC | 1 | Year |  | 3
| 4061 | FDD | 1 | Hour |  | 3
| 4062 | FDE | 1 | Minute |  | 3
| 4063 | FDF | 1 | Second |  | 3
| 4064 | FE0 | 2 | THD 3V Minimum |  | 3
| 4066 | FE2 | 1 | Month |  | 3
| 4067 | FE3 | 1 | Day |  | 3
| 4068 | FE4 | 1 | Year |  | 3
| 4069 | FE5 | 1 | Hour |  | 3
| 4070 | FE6 | 1 | Minute |  | 3
| 4071 | FE7 | 1 | Second |  | 3
| 4072 | FE8 | 2 | THD 3V Maximum |  | 3
| 4074 | FEA | 1 | Month |  | 3
| 4075 | FEB | 1 | Day |  | 3
| 4076 | FEC | 1 | Year |  | 3
| 4077 | FED | 1 | Hour |  | 3
| 4078 | FEE | 1 | Minute |  | 3
| 4079 | FEF | 1 | Second |  | 3
| 3840 | F00 | 240
1000 Hex : 10 Last Power supply cut off
| Address Dec. | Address Hex. | Word Count | Description | Unit | Function
Power supply cut off Level n-1
| 4096 | 1000 | 1 | Month |  | 3
| 4097 | 1001 | 1 | Day |  | 3
| 4098 | 1002 | 1 | Year |  | 3
| 4099 | 1003 | 1 | Hour |  | 3
| 4100 | 1004 | 1 | Minute |  | 3
| 4101 | 1005 | 1 | Second |  | 3
Power supply cut off Level n-2
| 4102 | 1006 | 6 |  |  | 3
Power supply cut off Level n-3
| 4108 | 100C | 6 |  |  | 3
Power supply cut off Level n-4
| 4114 | 1012 | 6 |  |  | 3
Power supply cut off Level n-5
| 4120 | 1018 | 6 |  |  | 3
Power supply cut off Level n-6
| 4126 | 101E | 6 |  |  | 3
Power supply cut off Level n-7
| 4132 | 1024 | 6 |  |  | 3
Power supply cut off Level n-8
| 4138 | 102A | 6 |  |  | 3
Power supply cut off Level n-9
| 4144 | 1030 | 6 |  |  | 3
Power supply cut off Level n-10
| 4150 | 1036 | 6 |  |  | 3
| 4096 | 1000 | 60
3000 Hex : AVG Power Historical
| Address Dec. | Address Hex. | Word Count | Description | Unit | Function
| 12288 | 3000 | 1 | PHIS : pointer on the most recent P value in the Historical table |  | 3
| 12289 | 3001 | 1 | QHIS : pointer on the most recent Q value in the Historical table |  | 3
| 12290 | 3002 | 3 | Pointer update datetime |  | 3
| 12293 | 3005 | 4500 | Zone P.1 P+ / P- values | Wh/10 | 3
| 16793 | 4199 | 4500 | Zone P.2 P+ / P- values | Wh/10 | 3
| 21293 | 532D | 4500 | Zone Q.1 Q+ / Q- values | VArh/10 | 3
| 25793 | 64C1 | 4500 | Zone Q.2 Q+ / Q- values | VArh/10 | 3
| 12288 | 3000 | 18005
See the application note : |  | A40 Power management
8000 Hex : AVG Voltage Historical
| Address Dec. | Address Hex. | Word Count | Description | Unit | Function
| 32768 | 8000 | 1 | Voltage Pointer |  | 3
| 32769 | 8001 | 3 | VHIS Update DateTime |  | 3
| 32772 | 8004 | 875 | 3U, 3V values | V/10 | 3
| 32768 | 8000 | 879
9000 Hex : AVG Frequency Historical
| Address Dec. | Address Hex. | Word Count | Description | Unit | Function
| 36864 | 9000 | 1 | Frecency POinter |  | 3
| 36865 | 9001 | 3 | FHIS Update DateTime |  | 3
| 36868 | 9004 | 8700 | F Value | F/100 | 3
| 36864 | 9000 | 8704

## Application Notes
APPLICATION NOTES
Historical data principle
The historical data can be read in two steps :
1 : Set the read pointer ( Write in the R1 register )
2 : Read the data buffer ( Read from the R2 register )
Command Area : Register R1 : Size 1 word
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
| R1 ( DEC) | R1 ( Hex) | 1 | Actions : 0x0001 : Reset reader pointer : locate the pointer on the most recent value stored 0xFFFE : Get Next data packet ( pointer is updated ) |  | W
| R1 | R1 | 1
When the register R1 is writing with the value 1 : automaticaly the data buffer ( Regsiter R2 ) is filled with the most recent value stored
After this operation, to read the next data Write 0XFFFE in the register R1
Data Area : Register R2 = R1 +10Hex : ( size 125 Words )
| Address Déc. | Address Hex. | Word Count | Description | Unit | Function
Header | R2(DEC) | R2(HEX) | 1 | Record count |  | R
| R2 +1 | R2 +1 | 1 | Record size : Y |  | R
| R2 +2 | R2 +2 | x | Data Header : this header may not exist according the historical type |  | R
Data Buffer | R3=R2 + 2 + x | R3=R2 + 2 + x | Y | Data |  | R
| R3 + Y | R3 + Y | Y | Data |  | R
| … | … | Y | Data |  | R
| …. | … | Y | Data |  | R
| R3+ n * Y | R3+ n * Y | Y | Data |  | R
The data area start always by two words :
1 : Record count : number of record present in the buffer
2 : Record Size : size of one data
Always read the complete area : function 16 with 125 Words
EN50160 Classification values
Sag classification
Duration t [ms]
Residual voltage u [%] | 20 < t < 200 | 200 < t < 500 | 500 < t < 1000 | 1000 < t < 5000 | 5000 < t <60000
90 > u >= 80 | 1 | 2 | 3 | 4 | 5
80 > u >= 70 | 6 | 7 | 8 | 9 | 10
70 > u >= 40 | 11 | 12 | 13 | 14 | 15
40 > u >= 5 | 16 | 17 | 18 | 19 | 20
5 > u | 21 | 22 | 23 | 24 | 25
Swell classification
Duration t [ms]
Swell voltage u [%] | 20 < t < 500 | 500 < t < 5000 | 5000 < t < 60000
u >= 120 | 26 | 27 | 28
120 > u >= 110 | 29 | 30 | 31
Power management for SM103E
DESCRIPTION OF TABLE
A power image is stored according to the frequency selected by the user in a table (T_HIS).
This storing can be synchronized with an external power demand (10 min., 15 min., 30 min.)
or an internal power demand (10 min. or 15 min.).
This cyclically completed table also comprises :
* power-on dates
* power-off dates
A P_HIS pointer gives the position of the next octet to be stored in P_HIS.
The energy image is stored in the table in 1 word.
The stored value corresponds to acquired energy, taking into account standardised inputs
of 5A and 400V (ignoring the transformer ratios of the current and voltage transformers).
The stored energy unit is 0.1 Wh.
Example :
Recording of energy is synchronized with a 10mn internal signal.
Where U1=U2=U3=230V and where I1=I2=I3=5A,
the energy over 10mn is 575 Wh.
Therefore, the stored energy is 5750 in the table.
he exact energy value is the stored value multiplied by the product of transformer ratios (CT*VT).
Description of date and time of power on
| T_HIS(n+0) | FXh | X=month
| T_HIS(n+1) | YYh | YY=day
| T_HIS(n+2) | ZZh | ZZ = hour
| T_HIS(n+3) | VVh | VV = minutes
When a word begins with " F ", this and the following word defines a power-on
Description of date and time of power off
| T_HIS(n+0) | EXh | X=month
| T_HIS(n+1) | YYh | YY=day
| T_HIS(n+2) | ZZh | ZZ = hour
| T_HIS(n+3) | VVh | VV = minutes
When a word begins with " E ", this and the following word defines a power-off.
Energy Description
| T_HIS(n+0) | XXh | XX = high order
| T_HIS(n+1) | YYh | YY= low order
General make-up of table
| Address in T_HIS |  | Value | Description
| OCTET N° |  | (Hex)
| 0 |  | F6 0A | power on 10/06
| 2 |  | 0A 03 | at 10h03
| 4 |  | 36 45 | at 10h10 energy not allocated CT and VT : 1389,3 Wh
| 6 |  | 87 51 | at 10h20 energy not allocated CT and VT : 3644,1 Wh
| 8 |  | 87 51 | at 10h30 energy not allocated CT and VT : 3644,1 Wh
| 10 |  | E6 0A | power off 10/06
| 12 |  | 0A 23 | at 10h35
| 14 |  | F6 0B | Power on 11/06
| 16 |  | 08 02 | at 08h02
| 18 |  | 36 45 | at 08h10 energy not allocated CT and VT : 1389,3 Wh
| 20 |  | ….